## Slide 1
8/20/25
US Territories Water Operator Training Series
Session 5: Drinking Water Regulations
www.efcnetwork.org
This program is made possible under a cooperative agreement with US EPA.

## Slide 2: Michelle Olson Water Utility Trainer and Specialist meolson@unm.edu

## Slide 3
This training series is funded by the US EPA

## Slide 4
Attendee Meeting Controls
Mute/unmute
  Click the microphone icon to unmute yourself to speak (if you are not speaking, don’t unmute)
Chat
  Click the chat icon and then use the dropdown next to send text instant messages to:
    Everyone publicly: messages will be visible to all participants
    Host only: messages will be sent only to the meeting host – Don’t send a chat to only me; I won’t have time to see it while presenting.
    Any attendee directly: message will be sent to the selected meeting participant only
Leave meeting
  Click on the leave icon to exit the ZOOM Meeting
1. Mute/unmute
2. Chat
3. Leave meeting

## Slide 5: Schedule for 2025:
Date | Topic
6/25/25 | Program Overview, Test Format, Study & Test Tips
7/9/25 | Drinking Water System Overview - (Source, Treatment, & Distribution)
7/23/25 | Basic Operator Math (+, -, /, x, Exponents and basic algebra)
8/6/25 | Applied Operator Math (Areas, Volume, Pressure)
8/20/25 | Drinking Water Regulations
9/3/25 | Source Water Characteristics
9/17/25 | Surface Water Intake Components, Well Components, and O&M
10/1/25 | Disinfection 1: Chloramines, UV, Chlorine Dioxide, Chlorine
10/15/25 | Disinfection 2: Chlorine Disinfection Application for Sodium Hypochlorite and Gas Chlorine (including storage and safety)
10/29/25 | Disinfection 3: Distribution System Application, Residual Measurement, Evaluation & Adjustment,
11/12/25 | Disinfection 4: Chlorine Disinfection Math
12/3/25 | Surface Water Treatment 1: Coagulation, Flocculation, Sedimentation (including chemistry, process controls, operations)
12/17/25 | Surface Water Treatment 2: Filtration
Links to recordings and material are available on our website at https://swefc.unm.edu/home/op-cert-trainings/

## Slide 6: Safe Drinking Water Act (SDWA)
August 20, 2025

## Slide 7: What is the Safe Drinking Water Act (SDWA)?
Territories
States
Tribes
Suppliers
Localities
Standards
Quality
Treatment
Requirements
Monitoring
Requirements

## Slide 8: Purpose of SDWA
Ensures the safe delivery of drinking water to consumers by a Public Water System (PWS).
Protects the public from naturally occurring and human-made contaminants that may be found in drinking water.

## Slide 9
SDWA – 1974
THMs – 1979
IESWTR and S1DBPR – 1998
2003 – S2DBPR & LT2ESWTR
FBRR – 2001
LT1ESWTR – 2002
2009 – GWR
SDWA Amendments – 1996
WI Crypto Outbreak – 1993
SDWA Amendments – 1986
2016 – RTCR
2024 – Revised LCR
History of SDWA
TCR & SWTR – 1989
PFAs

## Slide 10: SDWA
Defines Public Water Systems.
Establishes Regulatory Programs.
Establishes National Primary & Secondary Drinking Water Regulations.
Requires Communication with Consumers.
Outlines Prevention Approaches.

## Slide 11: Public Water System (PWS) Definition
Serves ≥ 25 people for at least 60 days out of the year.
OR
Provides water to at least 15 service connections.

## Slide 12: PWS Types
Community (C) – Serves at least 15 service connections or at least 25 residents year-round.
Non-Transient Non-Community (NTNC) – Serves at least 15 service connections or 25 of same people (not residents) for at least 6 months in the year (might not be year-round).
Transient Non-Community (TNC) – Serves at least 15 service connections or 25 people (not the same individuals) at least 60 days of the year.

## Slide 13: SDWA Regulatory Programs
Primacy
Direct Implementation

## Slide 14: Drinking Water Regulations
National Primary Drinking Water Regulations
Standards
Health
Based
National Secondary Drinking Water Regulations
Standards
Aesthetic
Based

## Slide 15
Maximum Contaminant
Level (MCL)

## Slide 16
Treatment Techniques:
May only be set if it is not “economically or technologically feasible to ascertain the level of the contaminant.”
An enforceable procedure or level of technological performance that public water systems must follow to ensure control of a contaminant.

## Slide 17
Ground Water Rule (GWR)
Filter Backwash Recycling Rule
Long Term 1 (LT1) and Long Term 2 (LT2) Enhanced Surface Water Treatment Rule
Chemical Contaminant Rule
Radionuclides Rule
Arsenic Rule
PFAS
Revised Total Coliform Rule (RTCR)
Stage 1 & 2 Disinfectants and Disinfection By-Products Rule (D/DBPR)
Lead & Copper Rule, Revisions, Improvements (LCR, LCRR, LCRI)
Know the Rules!

## Slide 18: National Secondary Drinking Water Regulations
Not enforceable by EPA

## Slide 19: Individual Contaminant Monitoring Schedules Are Based On:
System Type (C, NTNC, TNC)
Source Type (GW, SW, GUDI)
Treatment Type
Historical Water Quality Results

## Slide 21
SDWA Compliance Sampling Locations

## Slide 22
A) Source Water Monitoring

## Slide 23
Purpose – To target ground water systems that have E.coli contamination in their wells.
Requires sanitary surveys be conducted:
  Once every 3-years for Community water systems.
  Once every 5-years for Non-Community water systems.
Requires individual wells to be sampled
after a total coliform present sample or
fecal positive (E. coli) present sample.
Ground Water Rule

## Slide 24
Purpose – To protect public health by reducing waterborne diseases caused by microbial pathogens in public water systems that use surface water or groundwater under direct influence of surface water (GUDI).
Filtration of water
Requires sanitary surveys be conducted:
  Once every 3-years for unfiltered systems (rare).
  Once every 5-years for filtered systems.
Surface Water Treatment Rule

## Slide 25
Surface Water Treatment Rule cont.
Disinfection Requirements:
  For the removal of protozoans and viruses.
  Chlorine, chloramine, ozone, UV.
Requires Cryptosporidium Monitoring (every 3-6 years)
Sets Turbidity Standards
  Filtered systems:
    Turbidity must be ≤0.3 NTU in ≥95% of monthly samples.
    Maximum turbidity = 1 NTU at any time.
  Unfiltered systems (rare, must meet strict criteria):
    Continuous turbidity monitoring required.

## Slide 26: B) Entry Point Monitoring

## Slide 27: B) Entry Point Monitoring
Chemical and Radionuclides Rules
Purpose – To protect public health by monitoring for source water contaminants that may cause disease.
Representative of water served to all customers.
**Water is monitored before public consumption**

## Slide 28: Chemical and Radionuclides
Nitrates & Nitrites
  From septics, animals waste, fertilizer
Inorganic Contaminants (IOCs)
  Heavy metals, sodium, fluoride, cyanide, asbestos
Volatile Organics Contaminants (VOCs)
  Gasoline, brake fluid, oil, hydraulic fluid
Synthetic Organic Compounds (SOCs)
  Herbicides, pesticides, PCBs
Radionuclides (Gross Alpha & Beta, Rad 226/228, Uranium)
  Mining, naturally occurring, human-made sources
PFAS (HFPO-DA, PFBS, PFHxS, PFNA, PFOA, PFOS)
  Human-made sources
Acute Health Effects
Chronic Health Effects

## Slide 29: C) Distribution System Monitoring

## Slide 30: C) Distribution System Monitoring
Purpose – To qualify water quality in the distribution system.
Revised Total Coliform Rule (RTCR)
Disinfectants/Disinfection Byproducts Rules (D/DBPR)
Lead & Copper Rule (LCR, LCRR, LCRI)

## Slide 31: The Revised Total Coliform Rule (RTCR)
Which Systems Have to Sample?
Community
Non-Transient Non-Community
Transient
Non-Community

## Slide 32
Found in air, soil, and the intestinal tracts of warm-blooded animals.
Total coliform include all coliform bacteria:
  - Fecal Coliform (subset of total coliform)
  E.coli (subset of fecal coliform)
A group of mostly non-pathogenic bacteria.
What are total coliforms?

## Slide 33: The presence of coliforms indicate that the water may be contaminated with pathogens (organisms that can cause disease).
Types of Pathogens:
Protozoans (Giardia and Cryptosporidium)
Viruses (Hepatitis A, Rotavirus, Norovirus)
Bacteria (Gastroenteritis, Bacillary Dysentery, Typhoid Fever, Cholera, and Tuberculosis)
Cryptosporidium
Typhoid Fever
Hepatitis A
How do total coliforms act as an indicator?
Acute Health Effects

## Slide 34: How can Pathogens enter our Drinking Water Systems?
Source Contamination
Treatment Contamination
Distribution Contamination
Storage Contamination
Contamination

## Slide 35: RTCR Monitoring
Number of routine samples based on size of population served.
Routine samples collected monthly in distribution at representative sites, no exemptions.
Sampling is done by the water system.

## Slide 36: What do the Results Mean?
Total Coliform
Present or Absent (TC+ or TC -)
E. coli
Present or Absent (EC+ or EC-)

## Slide 37: What if the Routine sample results are TC and/or EC “Present”?
PWS must collect 3 repeat samples for each positive routine sample within 24 hours of being notified.
Original location.
Upstream location within 5 service connections.
Downstream location within 5 service connection

## Slide 38
Following Month:
Collect the regular number of routine samples

## Slide 39: RTCR Assessments
Level 1 Assessment: Evaluation of source water, treatment, distribution, and other operational practices that is completed by the system.
Level 2 Assessment: Detailed evaluation conducted by EPA or an approved third party. Additional sampling, inspections, etc. . . could be required.
Find & Fix

## Slide 40: Disinfectants/Disinfection Byproducts Rule (D/DBPR)
Which Systems Have to Sample?
*PWSs adding a disinfectant to the drinking water during any part of the treatment process.
Community
Non-Transient Non-Community

## Slide 41: Public Heath & Disinfection
Disinfectants inactivate pathogenic microorganisms.
Disinfectants react with substances naturally in water to form harmful Disinfection Byproducts (DBPs).
Both Disinfectants and DBPs produce negative health effects when present in excessive levels.

## Slide 42: Disinfectant Health Effects
Anemia
Other Short-Term Effects
Eye and Nose Irritation
Stomach Upset
Chronic Health Effect
Acute Health Effects
Disinfection Byproducts Health Effects
Anemia
Reproductive Problems
Central Nervous System Problems
Liver & Kidney Problems
Cancer
Chronic Health Effects
Microbials
Byproducts

## Slide 43: Types of Disinfectants
Chlorine
Chlorine Dioxide
Chloramines
Bromine
Ozone
Ultraviolet Light (UV)
Chemical
Physical
Most Widely Used

## Slide 44
Disinfection Byproducts Formation
Precursor in Water
Natural Organic Matter
+
Add Disinfectant
Chlorine
Chloramines
Ozone
Chlorine Dioxide
=
TTHMs & HAA5s
TTHMs & HAA5s
Bromate
Chlorite
DBPs
Higher DBPs formation during the warmer months!

## Slide 45
  Maximum Residual Disinfectant Level (MRDL)
  Chlorine MRDL = 4.0 mg/L
  Calculated based on a running annual average (RAA) of RTCR monthly samples.
1.) Residual Disinfectant Level
The amount of disinfectant left in the system after it has reacted with precursors in the water (free chlorine residual).
  Minimum Residual Disinfectant Level
    EPA recommends a minimum residual in distribution of 0.2 mg/L (required for surface water systems)

## Slide 46
DBPs Maximum Contaminant Levels (MCLs)
46
Trihalomethanes (THMs)
  4 containments
  MCL = 0.080 mg/L
Haloacetic Acids (HAA5)
  5 contaminants
  MCL= 0.060 mg/L
Chlorite (only if PWS uses chlorine dioxide)
  MCL = 1.0 mg/L
Bromate (only if PWS uses ozone)
  MCL = 0.010 mg/L

## Slide 47: The Lead & Copper Rule (LCR, LCRR, LCRI)
Which Systems Have to Sample?
Community
Non-Transient Non-Community

## Slide 48: What are the Lead & Copper rules?
The OG Lead & Copper Rule (LCR)
The Lead & Copper Rule Revisions (LCRR)
The Lead & Copper Rule Improvements (LCRI)

## Slide 49: Sources of Lead & Copper in Drinking Water
Galvanized Pipes
(in downstream locations of LSLs)
Lead Solder at Pipe Joints
Lead and Copper Pipes
Brass Fittings
The corrosion of household plumbing and fixtures

## Slide 50: Lead Health Effects
High Blood Pressure
Attention Deficit Disorders
Physical & Developmental Problems
Central Nervous System Disorders
Chronic Health Effects
Copper Health Effects
GI Distress
Wilkinson’s Disease Issues if above AL
Liver or Kidney Damage
Chronic Health Effect
Acute Health Effects

## Slide 51
Number of samples based on:
  Population size;
  Standard (6M) or Reduce (1/YR or 1/3YR) monitoring schedules.
Those on reduce schedules must collected June-September.
Sampling for Lead & Copper
Number of samples required (LCR & WQP)

## Slide 52: Where do we collect Lead & Copper samples?
At Consumers Taps: kitchen sinks breakroom sinks bathroom sinks
Samples are collected after at least a 6-hour hold time.
NOT when sample locations are inactive.
NOT at abandoned homes.
NOT at an entry point (EP).

## Slide 53
Action Levels (AL) - based on 90th percentiles
  Lead - 0.015 mg/L (ppm)
  Copper - 1.3 mg/L (ppm)
  *If 90% of sample results are at
  or below the AL value, no exceedance.
Understanding Lead & Copper Sample Results
GOAL = Zero for Lead

## Slide 54
Understanding Lead & Copper Sample Results
Site A | 0.001 mg/L
Site B | 0.003 mg/L
Site C | 0.002 mg/L
Site D | non-detect
Site E | 0.006 mg/L
Site F | 0.001 mg/L
Site G | 0.001 mg/L
Site H | 0.002 mg/L
Site I | 0.022 mg/L
Site J | 0.001 mg/L
Original Lead Results
Lead = 0.015 mg/L

## Slide 55
Understanding Lead & Copper Sample Results
1. Order the results from highest to lowest
Lowest Value
Highest Value
0.001 mg/L
0.003 mg/L
0.002 mg/L
non-detect
0.006 mg/L
0.001 mg/L
0.001 mg/L
0.002 mg/L
0.022 mg/L
0.001 mg/L
0.022 mg/L
0.006 mg/L
0.003 mg/L
0.002 mg/L
0.002 mg/L
0.001 mg/L
0.001 mg/L
0.001 mg/L
0.001 mg/L
non-detect
Original Lead Results
Reordered Results

## Slide 56
Understanding Lead & Copper Sample Results
2. Number the results with 1 being the lowest value, 2 being the next higher value on up
Lowest Value
Highest Value
10 | 0.022 mg/L
9 | 0.006 mg/L
8 | 0.003 mg/L
7 | 0.002 mg/L
6 | 0.002 mg/L
5 | 0.001 mg/L
4 | 0.001 mg/L
3 | 0.001 mg/L
2 | 0.001 mg/L
1 | non-detect
Reordered Results

## Slide 57
Understanding Lead & Copper Sample Results
3. Find the 90th percentile value
Lowest Value
Highest Value
Reordered Lead Results
  If 10 samples = 9th highest sample
  If 20 samples = 18th highest sample
  If 5 samples = avg 4th & 5th samples
# of samples x 0.9
(Example: 10 samples x 0.9 = 9th sample)
10 | 0.022 mg/L
9 | 0.006 mg/L
8 | 0.003 mg/L
7 | 0.002 mg/L
6 | 0.002 mg/L
5 | 0.001 mg/L
4 | 0.001 mg/L
3 | 0.001 mg/L
2 | 0.001 mg/L
1 | 0.001 mg/L
Lead = 0.015 mg/L

## Slide 58: What if an Action Level is Exceeded?
Source water monitoring for Lead & Copper
Water quality parameter (WQP) monitoring at EP & DS (compliance monitoring)
Public education
Determine optimal corrosion control treatment
Lead service line replacement
Under-sink fixture replacement
ALE

## Slide 59: SDWA Requires Consumer Communication
Public Notification Rule
Communicate
Water Utility Authority

## Slide 60: Public Notification (PN) Rule Types
Tier 1: Most Severe
Immediate health risk.
Public Notice must be issued within 24 hours.
Examples:
  Boil Water Advisory (Ecoli +).
  Nitrate exceedance (MCL=10mg/L).
  Lead exceedance (AL=15ug/L).
  TT violation.
Tier 2: Moderate Severity
Potential health risk.
Public Notice must be issued within 30 days.
Examples:
  Other MCLs not immediately affecting public health.
  Improperly treated water (TT failure).
  Failure to address deficiencies.
Tier 3: Important
No immediate health risk.
Public Notice must be issued within 1 year.
Examples:
  Administrative issues.
  Monitoring and reporting violations.

## Slide 61: SDWA Requires Consumer Communication
Consumer Confidence Report Rule

## Slide 62
Records include:
  Test results
  Mandates
  Other records
Records must be kept at or near the utility office (in close proximity).
Record Keeping Rule

## Slide 63
Different rules under SDWA require different record retention times.
Record Keeping Rule
Public Notices and CCRs: 3 yrs
Bacteriological & Turbidity: 5 yrs
Sanitary Survey Reports: 10 yrs
ChemRad & DBP analyses: 10 yrs
Lead and Copper: 12 yrs

## Slide 64: SDWA Summary
Establishes federal standards for safe levels of contaminants in public drinking water systems.
Includes measures to safeguard groundwater and surface water from contamination.
Requires water systems to monitor, test, and report water quality to authorities and the public.
The National Primary Drinking Water Regulations: https://www.ecfr.gov/current/title-40/chapter-I/subchapter-D/part-141

## Slide 65: Questions?

## Slide 66: CONTACT US
Physical Address
SWEFC/Civil Engineering Dept.
MSC01 1070
1 University of New Mexico
Albuquerque, New Mexico 87131-0001
http://swefc.unm.edu/
Michelle Olson
meolson@unm.edu