## Slide 1
10/2/25
US Territories Water Operator Training Series
Session 8: An Introduction to Disinfection (part 1 of 4)
www.efcnetwork.org
This program is made possible under a cooperative agreement with US EPA.

## Slide 2: Matt Ziegler Program Director
Your trainer for today

## Slide 3
This training series is funded by the US EPA

## Slide 5: Schedule for 2025:
Links to recordings and material are available on our website at https://swefc.unm.edu/home/op-cert-trainings/
Date | Topic
6/26/25 | Program Overview, Test Format, Study & Test Tips
7/10/25 | Drinking Water System Overview - (Source, Treatment, & Distribution)
7/24/25 | Basic Operator Math (+, -, /, x, Exponents and basic algebra)
8/7/25 | Applied Operator Math (e.g. Areas, Volume, Flow Rates, Detention Time, Pressure/Hydraulic Head)
8/21/25 | Drinking Water Regulations
9/4/25 | Source Water Characteristics
9/18/25 | Surface Water Intake Components, Well Components, and O&M
10/2/25 | Disinfection 1: Chloramines, UV, Chlorine Dioxide, Chlorine
10/16/25 | Disinfection 2: Chlorine Disinfection Application for Sodium Hypochlorite and Gas Chlorine (including storage and safety)
10/30/25 | Disinfection 3: Distribution System Application, Residual Measurement, Evaluation & Adjustment,
11/13/25 | Disinfection 4: Chlorine Disinfection Math
12/4/25 | Surface Water Treatment 1: Coagulation, Flocculation, Sedimentation (including chemistry, process controls, operations)
12/18/25 | Surface Water Treatment 2: Filtration

## Slide 6: https://swefc.unm.edu/home/op-cert-trainings/

## Slide 7: Sign in for every session to ensure you get credit for attending

## Slide 8: An Introduction to Disinfection
Disinfection

## Slide 9: What is Disinfection?
Disinfection is the inactivation of pathogenic microorganisms
Sterilization is the destruction of all living organisms and is NOT disinfection

## Slide 10: Disease Causing Viruses
Hepatitis A
Rotavirus
Norovirus
Gastroenteritis
Fatigue, Nausea, Abdominal Pain,
Loss of Appetite, Low-grade Fever
Gastroenteritis
Acute Health Effects
Notes: Hepatitis A Virus from https://www.fda.gov/food/foodborne-pathogens/hepatitis-virus-hav
Rotovirus from Wikipedia By Dr Graham Beards, CC BY 3.0, https://commons.wikimedia.org/w/index.php?curid=5535228
Norovirus from CDC.gov

## Slide 11: Disease Causing Bacteria
Escherichia coli
Shigella dysenteriae
Salmonella typhi
Vibrio cholerae
Mycobacterium tuberculosis
Gastroenteritis
Bacillary Dysentery
Typhoid Fever
Cholera
Tuberculosis
Acute Health Effects
Notes: Ecoli image on Wikipedia by By Credit: Rocky Mountain Laboratories, NIAID, NIH - NIAID: These high-resolution (300 dpi) images may be downloaded directly from this site. All the images, except specified ones from the World Health Organization (WHO), are in the public domain. For the public domain images, there is no copyright, no permission required, and no charge for their use., Public Domain, https://commons.wikimedia.org/w/index.php?curid=104228
Shigella Image on Wikipedia by By Armed Forces Institute of Pathology, AFIP - https://phil.cdc.gov/Details.aspx?pid=22229, Public Domain, https://commons.wikimedia.org/w/index.php?curid=77323598
"Salmonella" by National Institutes of Health (NIH) is licensed under CC BY-NC 2.0
"Vibrio bacteria" by National Institutes of Health (NIH) is licensed under CC BY-NC 2.0
"Mycobacterium tuberculosis Bacteria" by NIAID is licensed under CC BY 2.0

## Slide 12: Disease Causing Protozoa
Giardia lamblia
Cryptosporidium
Giardiasis
Cryptosporidiosis
Acute Health Effects
Notes: Giardia image from Wikipedia By Dr. Stan Erlandsen (1988) - Public Health Image Library (PHIL) -- image #11632, Public Domain, https://commons.wikimedia.org/w/index.php?curid=9779989
Crypto cyst on Wikimedia Av Centers for Disease Control and Prevention - https://www.cdc.gov/parasites/crypto/, CC BY-SA 4.0, https://commons.wikimedia.org/w/index.php?curid=68364333

## Slide 13: How can pathogens enter our drinking water systems?
Source Contamination
Treatment Contamination
Storage Contamination
Distribution Contamination
DISINFECTION

## Slide 14: WATER TREATMENT
The second barrier to preventing waterborne disease using the Multiple Barrier Approach

## Slide 15: Types of Disinfectants
Chloramines
Ozone
Chlorine
Chlorine Dioxide
Ultraviolet Light (UV)
Chemical
Physical
Notes: Chlorine Dioxide Public Domain, https://commons.wikimedia.org/w/index.php?curid=832546
Chloramine molecule from wikipedia by By Benjah-bmm27 - Own work, Public Domain, https://commons.wikimedia.org/w/index.php?curid=1264855

## Slide 16: Chemical Disinfection Process
Oxidation – the oxidant steals electrons from the virus or cell’s enzymes so they can no longer perform metabolic functions

## Slide 17: Chloramine Disinfection
Used as a drinking water disinfectant for >90 years
Used by >1 in 5 larger systems in the U.S.
Generated on-site when ammonia is added to water containing chlorine
Chemical
I’m #2!!!

## Slide 18
From Guidelines for Canadian Drinking Water Quality
Technical Document Chloramines
Chloramine Disinfection Objectives
Maximize monochloramines
Minimize free ammonia
Prevent excess dichloramines
Prevent breakpoint
Measure TOTAL Chlorine
Notes: https://www.canada.ca/content/dam/hc-sc/images/services/publications/healthy-living/guidelines-canadian-drinking-water-quality-guideline-technical-document-chloramines/fig1-eng.jpg

## Slide 19: Chloramine Disinfection
Advantages
Used as a secondary disinfectant with a long-lived combined chlorine residual that produces fewer halogenated disinfection byproducts
Disadvantages
Less effective as a primary disinfectant than chlorine
Can change water chemistry and impact lead & copper pipes – follow EPA guidance
Taste & odor issues

## Slide 20
Chloramine Disinfection SDWA Regulations
Maximum Residual Disinfectant Level (MRDL) = 4.0 mg/L
Subject to the Stage 1 & 2 Disinfectant and Disinfection By Products Rules (D/DBPR)
  Monitor for Total Trihalomethanes (MCL = 80 ug/L)
  Monitor for Haloacetic Acids (MCL = 60 ug/L)
Notes: https://www.canada.ca/content/dam/hc-sc/images/services/publications/healthy-living/guidelines-canadian-drinking-water-quality-guideline-technical-document-chloramines/fig1-eng.jpg

## Slide 21: Chlorine Dioxide
Yellow to reddish-yellow gas
On-site generation
Used by ~5% of large water systems in the U.S.
Chemical
Notes: Graphic from: https://www.sciencedirect.com/science/article/pii/S194439862500356X
Chlorine dioxide drinking water pre-oxidation and disinfection: A review of its effectiveness, mechanisms, and disinfection by-products
Author: M. Mzinyathi,V. Muthuraj,E.O. Ajala,B. Kakavandi,S. Janse van Rensburg,T.T.I. Nkambule,G. Mamba
Publication: Desalination and Water Treatment
Publisher: Elsevier
Date: July 2025

## Slide 22: Chlorine Dioxide Disinfection
Advantages
Very effective disinfectant against viruses, bacteria, and cysts
Disadvantages
Storage and handling hazards of chemical precursors
Improves taste, odor, & color caused by chlorophenols and algae
Removes Fe & Mn
Less likely to form DBPs
pH neutral
More volatile than liquid chlorine
Chlorite byproduct (daily monitoring)
Higher initial costs

## Slide 23: Ozonation
Effective disinfectant for relatively clean source waters
Onsite generation with UV and compressed air
Can damage lungs due to oxidizing effect on tissue
  PPE = canister (carbon) respirator at low concentrations (0.3-10 ppm)
Submerged Bubbler
Chemical

## Slide 24: Ozone Disinfection
Advantages
Rapid and effective against Crypto oocysts, E.coli and other pathogens
Disadvantages
Quick decomposition
Removes precursors of organic DBPs
No residual
Bromate byproduct (monthly monitoring)

## Slide 25: Ultraviolet Light
250 nm wavelength
Physical
Notes: Bulbs are generally placed in-line with the flow of water, which is at a shallow depth, so all the water flows a close distance to the bulbs for a period of time.
SWEFC Photos

## Slide 26: UV Disinfection
Advantages
Effective against Crypto and Giardia
Disadvantages
Source water needs to be clean
Short contact time
No chemical handling
No halogenated DBP formation
User friendly with minimal maintenance
Ineffective against some bacteria (adenovirus) and bacterial spores
Organisms may undergo self-repair
No residual in distribution

## Slide 27: Chlorine Disinfection
Most Common Disinfectant in the U.S.
Chemical

## Slide 28: Types of Chlorine
Chlorine (Cl2)
Gas
Calcium Hypochlorite
(CaOCl)
Liquid
10-12.5% (30-50 gallon drums)
Compresses to a liquid
Bleach = 4.75-8.25%
~1 month shelf life
Sodium Hypochlorite
(NaOCl)
Solid
1-3% mixed by operator
~1-year shelf life
Handling hazards
100% chlorine
  1% = 10,000 mg/L Cl2
Notes: Cl2 gas photo https://hu.wikipedia.org/wiki/Szerkeszt%C5%91vita:Boro/Arch%C3%ADv03

## Slide 29: On-site Generation of Sodium Hypochlorite
NaCl + H2O + energy = NaOCl + H2
Creates low concentration NaOCl (0.4-0.8 ppm)

## Slide 30: On-site Generation of Sodium Hypochlorite

## Slide 31: On-site Generation of Sodium Hypochlorite

## Slide 32: Chlorine Disinfection
Advantages
High germicidal power
Disadvantages
Used up quickly
Highly soluble in water
Cost less than other methods & readily available
Measure residual to evaluate effectiveness
Strong residual protection in distribution
Formation of disinfection byproducts (DBPs)
Increases corrosiveness
Risk of accidental release

## Slide 33
Chlorine Disinfection
SDWA Regulations
Maximum Residual Disinfectant Level (MRDL) = 4.0 mg/L
Subject to the Stage 1 & 2 Disinfectant and Disinfection By Products Rules (D/DBPR)
  Monitor for Total Trihalomethanes (MCL = 80 ug/L)
  Monitor for Haloacetic Acids (MCL = 60 ug/L)
Same As Chloramines
Notes: https://www.canada.ca/content/dam/hc-sc/images/services/publications/healthy-living/guidelines-canadian-drinking-water-quality-guideline-technical-document-chloramines/fig1-eng.jpg

## Slide 34
From Nature.com
Chlorine Disinfection Objectives
Reach breakpoint
Minimize chloramines and combined chlorine
Measure FREE Chlorine
Demand
Notes: https://www.canada.ca/content/dam/hc-sc/images/services/publications/healthy-living/guidelines-canadian-drinking-water-quality-guideline-technical-document-chloramines/fig1-eng.jpg

## Slide 35
It’s the difference that causes burning eyes and skin rashes after using a pool or hot tub
Pungent to acrid smell
Chloramine odor (Often confused w/ strong “chlorine” odor)
Oooh… That Smell!
Clean, fresh smell
Slight chlorine odor

## Slide 36: How Chlorine Disinfection Works

## Slide 37: Chlorine & Water First Reaction
Cl2 + H2O = HOCl + HCl
Cl2 = Chlorine
H2O = Water
HOCl = Hypochlorous Acid
HCl = Hydrochloric Acid

## Slide 38: Chlorine & Water Second Reaction
HOCl is more effective as a disinfectant than OCl- (100-300 times greater)
HOCl = H+ + OCl-
HOCl = Hypochlorous Acid
H+ = hydrogen ion
OCl- = hypochlorite ion

## Slide 39: Factors that Affect Chlorine Disinfection

## Slide 40: Factors That Affect Chlorine Disinfection
pH
  Better disinfection occurs at lower pHs

## Slide 41: Factors That Affect Chlorine Disinfection
The colder the water, the longer the contact time
The warmer the water, the shorter the contact time
The warmer the water and the surrounding environment, the more chlorine dissipates into the atmosphere
Water Temperature

## Slide 42: Factors That Affect Chlorine Disinfection
Viruses are much harder to kill than bacteria and require higher chlorine dosages
Some protozoans are extremely resistant to chlorine and may not be affected at all
  Cryptosporidium
  Giardia
*That’s why surface water systems and GWUDI systems must also provide filtration in addition to disinfection*
Type of Organism
Notes: 42

## Slide 43: Factors That Affect Chlorine Disinfection
Organic Materials
Minerals
Turbidity
Interfering agents increase the chlorine demand in the distribution system
Interfering Agents
Notes: 43

## Slide 44: Factors That Affect Chlorine Disinfection
Nitrogen compounds present in the water combine with HOCl and form chloramines
  Inorganic ammonia
  Organic proteins and amino acids
Chloramines are Combined Residual Chlorine
Combined chlorine is available for disinfection
Type of Residual

## Slide 45
The amount of hypochlorous acid (HOCl) or hypochlorite ion (OCl-) that has not combined with nitrogen compounds and is still available is measured as:
Free Residual Chlorine
Type of Residual
Free chlorine is available for disinfection
Factors That Affect Chlorine Disinfection

## Slide 46: Factors That Affect Chlorine Disinfection
FREE RESIDUAL CHLORINE
IS THE BEST DISINFECTANT
Type of Residual
Required minimum of 0.2 mg/L everywhere in the distribution system if surface water
Recommend 0.2 mg/L everywhere if ground water
Higher at the EP
This level will vary with different systems

## Slide 47: Chlorine Disinfection Terminology Review

## Slide 48: Chlorine Dosage
The total amount of chlorine fed into a volume of water (expressed as mg/L)
Most operators record pounds or gallons per day. This is the FEED RATE, not the dosage.
DOSAGE = DEMAND + RESIDUAL

## Slide 49: Chlorine Demand
The difference between the amount of chlorine fed (dosage) and the residual chlorine remaining
The amount of chlorine consumed or bound up by material in the water (expressed as mg/L)
This chlorine is NOT available for residual (free or total)
DEMAND = DOSAGE - RESIDUAL
Notes: Chlorine reacts with iron, manganese, organic matter, turbidity & microorganisms. This is the demand

## Slide 50: Chlorine Residual
The amount of chlorine remaining after the chlorine demand is satisfied (expressed as mg/L)
This chlorine IS available for further disinfection
RESIDUAL = DOSAGE - DEMAND

## Slide 51: Three Types of Chlorine Residual
Total
Combined
Free
TOTAL = COMBINED + FREE

## Slide 52: Calculate Chlorine Residual
Calculate the residual chlorine if the demand is 2.0mg/L and the dosage is 2.8 mg/L
Residual Cl2 = Dosage – Demand
Residual Cl2= 2.8 mg/l – 2.0 mg/L
Residual Cl2= 0.8 mg/L
What do we know?
Residual Cl2 = Dosage – Demand
Demand = 2.0 mg/L
Dosage = 2.8 mg/L
This equation can be re-arranged to solve for any of the given parameters by isolating the unknown
Residual = Dosage – Demand
Dosage = Residual + Demand

## Slide 53: Next time:
Links to recordings and material are available on our website at https://swefc.unm.edu/home/op-cert-trainings/
Date | Topic
6/26/25 | Program Overview, Test Format, Study & Test Tips
7/10/25 | Drinking Water System Overview - (Source, Treatment, & Distribution)
7/24/25 | Basic Operator Math (+, -, /, x, Exponents and basic algebra)
8/7/25 | Applied Operator Math (e.g. Areas, Volume, Flow Rates, Detention Time, Pressure/Hydraulic Head)
8/21/25 | Drinking Water Regulations
9/4/25 | Source Water Characteristics
9/18/25 | Surface Water Intake Components, Well Components, and O&M
10/2/25 | Disinfection 1: Chloramines, UV, Chlorine Dioxide, Chlorine
10/16/25 | Disinfection 2: Chlorine Disinfection Application for Sodium Hypochlorite and Gas Chlorine (including storage and safety)
10/30/25 | Disinfection 3: Distribution System Application, Residual Measurement, Evaluation & Adjustment,
11/13/25 | Disinfection 4: Chlorine Disinfection Math
12/4/25 | Surface Water Treatment 1: Coagulation, Flocculation, Sedimentation (including chemistry, process controls, operations)
12/18/25 | Surface Water Treatment 2: Filtration

## Slide 54
CONTACT INFORMATION
Department of Civil Engineering MSC01 1070
1 University of New Mexico
Albuquerque, NM 87131
505-277-0644
swefc@unm.edu
http://swefc.unm.edu
SW EFC email: swefc@unm.edu