## Slide 1
10/30/25
US Territories Water Operator Training Series
Session 10: Disinfection 3: Distribution System Application, Residual Measurement, Evaluation & Adjustment (part 3 of 4)
www.efcnetwork.org
This program is made possible under a cooperative agreement with US EPA.

## Slide 2: Tucker Colvin Research Scientist tcovin@unm.edu

## Slide 3
This training series is funded by the US EPA

## Slide 5: Schedule for 2025:
Links to recordings and material are available on our website at https://swefc.unm.edu/home/op-cert-trainings/
Date | Topic
6/26/25 | Program Overview, Test Format, Study & Test Tips
7/10/25 | Drinking Water System Overview - (Source, Treatment, & Distribution)
7/24/25 | Basic Operator Math (+, -, /, x, Exponents and basic algebra)
8/7/25 | Applied Operator Math (e.g. Areas, Volume, Flow Rates, Detention Time, Pressure/Hydraulic Head)
8/21/25 | Drinking Water Regulations
9/4/25 | Source Water Characteristics
9/18/25 | Surface Water Intake Components, Well Components, and O&M
10/2/25 | Disinfection 1: Chloramines, UV, Chlorine Dioxide, Chlorine
10/16/25 | Disinfection 2: Chlorine Disinfection Application for Sodium Hypochlorite and Gas Chlorine (including storage and safety)
10/30/25 | Disinfection 3: Distribution System Application, Residual Measurement, Evaluation & Adjustment,
11/13/25 | Disinfection 4: Chlorine Disinfection Math
12/4/25 | Surface Water Treatment 1: Coagulation, Flocculation, Sedimentation (including chemistry, process controls, operations)
12/18/25 | Surface Water Treatment 2: Filtration

## Slide 6: https://swefc.unm.edu/home/op-cert-trainings/

## Slide 7: Sign in for every session to ensure you get credit for attending

## Slide 8: Today’s Agenda
CT
Distribution System Application
Residual Measurement
Residual Evaluation
Dosage Adjustment
Repairing Mains

## Slide 9
DOSAGE = DEMAND + RESIDUAL
Total amount of chlorine fed into a volume of water (mg/L)
Chlorine consumed by material in the water (mg/L)
NOT available for disinfection
NO residual chlorine
Chlorine remaining after demand is satisfied (mg/L)
IS available for disinfection

## Slide 11
CT
= Concentration x Time
Chlorine takes time to interact with and inactivate organisms. CT must be met to ensure affective inactivation.
The higher the concentration the less time needed.
The more time available the lower the required concentration.
Notes: A certain CT must me met before water is released back into the environment. This ensures that the chlorine has had sufficient time to react with all the pathogens. The chlorine concentration and time are inversely related, meaning that if you have a higher concentration of chlorine in the water, you don’t need as long of a time for it to react. Alternatively, if your water is in contact with your chlorine for a long period of time, you don’t need as high of a concentration of chlorine.
SWEFC Photo

## Slide 12: Baffling factor indicates the degree of short circuiting.

## Slide 13
Average baffling
Superior baffling

## Slide 14: Unbaffled tank B.F = 0.1 to 0.3
2. Tank with baffles B.F. = 0.5 to 0.7
Pipeline flow: B.F. = 1.0
Plug flow

## Slide 15: What is the CT of a system with the following information?
Chlorine concentration at EP of 0.5 mg/L
28 minutes in clearwell between chlorination and EP
Clearwell baffling factor of 0.3
CT = Concentration x (time x baffling factor)
CT = 0.5 mg/L x (28 minutes x 0.3)
CT = 0.5 mg/L x 8.4 minutes
CT = 4.2 mg-min/L
Is this CT sufficient?

## Slide 16: CT table - Virus inactivation with chlorine
In our example:
CT = 4.2 mg-min/L
Temperature = 15°C
pH = 8.4
4 log removal of viruses was achieved

## Slide 17
Understanding Log Treatment Levels
3 log treatment means 99.9% removal or inactivation.
4 log treatment means 99.99% removal or inactivation
The term log refers to an exponent of 10
Illustrative Example
A quantity of raw water contains 1,000,000 microbes and receives 4-log treatment to remove 99.99%.
1,000,000 microbes – [1,000,000 x 0.9999] = 100 microbes remaining
Take aways:
  The quantity of 10⁶ microbes was reduced to 10².
  The reduction factor is 10,000 [10,000 x 100 = 1,000,000]
  This reduction factor can be expressed as 10⁴, or 4-log

## Slide 18
Notes: https://nepis.epa.gov/Exe/ZyPDF.cgi?Dockey=200022IP.txt

## Slide 19: Poll: What types of disinfectant do you use at your plant?
Chlorination
Chloramination
Chlorine dioxide
Ozone
UV

## Slide 21
Parameter | Value
Diameter of pipe to First Customer (inches) | 6
Length of pipe to First Customer (feet) | 900
Volume of pipe to First Customer (gallons) | 1321.16
Peak flow to First Customer (gpm) | 150
Total contact time to First Customer (minutes) | 8.8
Temperature at First Customer (°F) | 77
Temperature at First Customer (°C) | 25
pH at First Customer | 7.9
CT from table - based on water temperature & pH (mg-min/L) | 2
Minimum Free Chlorine Residual Concentration Required at First Customer (mg/L) | 0.23

## Slide 22: Poll: Are you a ground water or surface water system?
Groundwater
Surface water
Poll: Have you ever calculated your CT?
Yes
No

## Slide 23: What is the log removal of a system with the following information?
Chlorine concentration at first customer of 0.41 mg/L
At peak flow, 40 minutes in clearwell with baffling factor of 0.2
At peak flow, 12 minutes in pipe going to first customer (baffling factor of 1.0)
Minimum temperature of 5°C
Maximum pH of 7.9
1 log removal
2 log removal
3 log removal
4 log removal

## Slide 24: What is the log removal of a system with the following information?
Chlorine concentration at first customer of 0.41 mg/L
At peak flow, 20 minutes in clearwell with baffling factor of 0.2
At peak flow, 4 minutes in pipe going to first customer (baffling factor of 1.0)
Minimum temperature of 11°C
Maximum pH of 7.9
CT = Concentration x Time
CT = 0.41 mg/L x 8 min
CT = 3.28 mg-min/L
Time = time in clearwell x baffling factor + time in pipe x baffling factor
Time = 20 minutes x 0.2 + 4 minutes x 1
Time = 4 minutes + 4 minutes
Time = 8 minutes
B. 2 log removal achieved

## Slide 25: Disinfection byproducts
Disinfectant reacts with naturally present substances in the water
  Fulvic and humic acids
  Amino acids
  Organic matter
  Iodide
  Bromide
DBPS include:
  Trihalomethanes (THMs)
  Haloacetic acids (HAAs)
  Bromate
  Chlorite
  Other non-regulated DBPs
Microbials
Byproducts

## Slide 26: Testing for chlorine residuals

## Slide 27: Testing For Chlorine Residuals

## Slide 28: Testing For Chlorine Residuals
DPD test
Must be tested within 15 minutes of sampling
Reagent is added and compared to the blank with a color wheel or a spectrometer/colorimiter
Reagent for free and total residual

## Slide 29
School
Senior Center
Hospital
Casino
$$$$$$
Legend
Well
Tank
House
Building
Store
29
Cl
Distribution system

## Slide 30: Distribution protection
Important distribution control measures
Physical integrity of the distribution system
Continuous positive water pressure (between 20 and 100 psi)
Maintain a chlorine residual (at least 0.20 mg/L)
  Contamination events require a source (contaminated groundwater), a pathway (pipe crack), and a mechanism (low pressure event).
  After initial disinfection, maintaining a free chlorine residual in the distribution system is a final barrier to protect against contamination, but once the residual is used up, there is no more disinfecting power.
  Multiple studies correlate water borne disease occurrences with main breaks, main repairs, and low pressure events.

## Slide 31
Biofilms protect pathogenic microbes from harsh environmental factors, including chlorine, shear stress, heat, inhibitors, and detergents, allowing them to survive (Hemdan et al., 2021).
EPS – Extracellular polymeric substances – gel like substances secreted by bacteria

## Slide 32
Waterville Residual Measurement
School
Senior Center
Hospital
Casino
$$$$$$
Legend
Well
Tank
House
Building
Store
Cl

## Slide 33: Which customers do we need to consider?
First customer (CxT)
Dead ends
Far ends of the distribution system
Susceptible populations
  Hospitals, dialysis clinics, schools

## Slide 34
Waterville Residual Measurement
School
Senior Center
Hospital
Casino
$$$$$$
Legend
Well
Tank
House
Building
Store
1st customer
Cl
First Customer – C x T

## Slide 35
Waterville Residual Measurement
School
Senior Center
Hospital
Casino
$$$$$$
Legend
Well
Tank
House
Building
Store
Cl
Dead Ends

## Slide 36: Dead Ends
Chlorine concentrations will be variable compared to the rest of distribution
Flush dead ends to ensure good chlorine levels - amount and timing depends on system
Increased biofilm growth
Increased disinfection byproduct formation (DBPs)
LeChevallier et al. (1996) found that distribution systems that have dead-ends with free chlorine residuals less than 0.2 mg/L or chloramine levels less than 0.5 mg/L had substantially more coliform occurrences (system-wide) than systems maintaining higher residuals.

## Slide 37
Chlorine residual decreases
Total Trihalomethanes increase

## Slide 38
Waterville Residual Measurement
School
Senior Center
Hospital
Casino
$$$$$$
Legend
Well
Tank
House
Building
Store
Cl
Far Ends of Distribution

## Slide 39: Far Ends of Distribution
Maintain 0.2 mg/L minimum
May need to increase chlorine at EP to make sure good residual at ends

## Slide 40: Measuring Residual Where and When?
After treatment (EP)
Process Control – Daily
SDWA Compliance Samples – according to compliance schedule
Distribution
RTCR Sites – Monthly
DBP Sites –according to compliance schedule
First Customer – Daily
Dead Ends – Daily
Long Runs – Daily
Far Ends of Distribution – Daily
Susceptible Populations – Daily

## Slide 41: Chlorine Residual Goals
Chlorine Disinfection & Daily Operations

## Slide 42: Written Goals Change How You Operate

## Slide 43: Goals Are Not Set in Stone
GOALS CAN BE ADDED OR REMOVED
OR ADJUSTED OVER TIME
GOALS CAN BE CHANGED

## Slide 44: SMART Goals

## Slide 45: How much free residual do we need to protect the customers?

## Slide 46
What is your goal for free residual chlorine at the EP?

## Slide 47
What is your goal for free residual chlorine at the first customer?

## Slide 48
What is your goal for free residual chlorine at dead ends?

## Slide 49
Under what conditions would you turn up your chlorine feed rate?

## Slide 50
Under what conditions would you turn down your chlorine feed rate?

## Slide 51: Disinfecting Water Mains

## Slide 59: Next time:
Links to recordings and material are available on our website at https://swefc.unm.edu/home/op-cert-trainings/
Date | Topic
6/26/25 | Program Overview, Test Format, Study & Test Tips
7/10/25 | Drinking Water System Overview - (Source, Treatment, & Distribution)
7/24/25 | Basic Operator Math (+, -, /, x, Exponents and basic algebra)
8/7/25 | Applied Operator Math (e.g. Areas, Volume, Flow Rates, Detention Time, Pressure/Hydraulic Head)
8/21/25 | Drinking Water Regulations
9/4/25 | Source Water Characteristics
9/18/25 | Surface Water Intake Components, Well Components, and O&M
10/2/25 | Disinfection 1: Chloramines, UV, Chlorine Dioxide, Chlorine
10/16/25 | Disinfection 2: Chlorine Disinfection Application for Sodium Hypochlorite and Gas Chlorine (including storage and safety)
10/30/25 | Disinfection 3: Distribution System Application, Residual Measurement, Evaluation & Adjustment,
11/13/25 | Disinfection 4: Chlorine Disinfection Math
12/4/25 | Surface Water Treatment 1: Coagulation, Flocculation, Sedimentation (including chemistry, process controls, operations)
12/18/25 | Surface Water Treatment 2: Filtration

## Slide 60
CONTACT INFORMATION
Department of Civil Engineering MSC01 1070
1 University of New Mexico
Albuquerque, NM 87131
505-277-0644
swefc@unm.edu
http://swefc.unm.edu
SW EFC email: swefc@unm.edu