## Slide 1
11/13/25
US Territories Water Operator Training Series
Session 11: Disinfection 4 Chlorine Disinfection Math
www.efcnetwork.org
This program is made possible under a cooperative agreement with US EPA.

## Slide 2: Michelle Olson Water Utility Trainer and Specialist meolson@unm.edu

## Slide 3
This training series is funded by the US EPA

## Slide 4
Attendee Meeting Controls
Mute/unmute
  Click the microphone icon to unmute yourself to speak (if you are not speaking, don’t unmute)
Chat
  Click the chat icon and then use the dropdown next to send text instant messages to:
    Everyone publicly: messages will be visible to all participants
    Host only: messages will be sent only to the meeting host – Don’t send a chat to only me; I won’t have time to see it while presenting.
    Any attendee directly: message will be sent to the selected meeting participant only
Leave meeting
  Click on the leave icon to exit the ZOOM Meeting
1. Mute/unmute
2. Chat
3. Leave meeting

## Slide 5: Schedule for 2025:
Date | Topic
6/26/25 | Program Overview, Test Format, Study & Test Tips
7/10/25 | Drinking Water System Overview - (Source, Treatment, & Distribution)
7/24/25 | Basic Operator Math (+, -, /, x, Exponents and basic algebra)
8/7/25 | Applied Operator Math (Areas, Volume, Pressure)
8/21/25 | Drinking Water Regulations
9/4/25 | Source Water Characteristics
9/18/25 | Surface Water Intake Components, Well Components, and O&M
10/2/25 | Disinfection 1: Chloramines, UV, Chlorine Dioxide, Chlorine
10/16/25 | Disinfection 2: Chlorine Disinfection Application for Sodium Hypochlorite and Gas Chlorine (including storage and safety)
10/30/25 | Disinfection 3: Distribution System Application, Residual Measurement, Evaluation & Adjustment,
11/13/25 | Disinfection 4: Chlorine Disinfection Math
12/4/25 | Surface Water Treatment 1: Coagulation, Flocculation, Sedimentation (including chemistry, process controls, operations)
12/18/25 | Surface Water Treatment 2: Filtration
Links to recordings and material are available on our website at https://swefc.unm.edu/home/op-cert-trainings/

## Slide 6: Disinfection 4: Chlorine Disinfection Math
Solid Concentrations and Chemical Solutions
Specific Gravity
Feed Rate

## Slide 7: Solids Concentration & Chemical Solutions
Notes: "bucket chemistry - mixing ferrous sulphate with cyanide residues" by Leo Reynolds is licensed under CC BY-NC-SA 2.0

## Slide 8
Solute
(Hypochlorite Salt)
Solvent
(Water)
Chemical Solutions: A homogenous mixture of at least two substances.
Chemical Solution
(Hypochlorite Solution)
Notes: “food-46573_1280” and “water-305656_1280” by Clker-Free-Vector-Images, Pixabay

## Slide 9
Chemical Solutions
Add hypochlorite salt to the water.
Notes: “powder-4617732_1280” by one94 and “water-305656_1280” by Clker-Free-Vector-Images, Pixabay

## Slide 10
Chemical Solution
Chemical Solutions
Mix until solute is completely dissolved.
Now we have our hypochlorite solution.
Notes: “spoon-41028_1280” and “water-305656_1280” by Clker-Free-Vector-Images, Pixabay

## Slide 11: Solids Concentration & Chemical Solutions
Solids concentration is the amount of dry chemical by weight (milligrams) mixed with an amount of water by volume (Liters) to make a chemical solution.

## Slide 12: Solids Concentration & Chemical Solutions
Solids concentration is the amount of dry chemical by weight (milligrams) mixed with an amount of water by volume (Liters) to make a chemical solution.

## Slide 13: Solids Concentration & Chemical Solutions
What ways are concentration expressed?
mg/L
  Weight of Solids (mg)/Volume of Liquid (L)
Parts per million (ppm)
  ppm = mg/L
  10 ppm = 10 mg/L
Purity (%)
  (Masschemical)/(Masssample) x 100%
  1% = 10,000 mg/L = 10,000 ppm
  10% NaClO solution = 100,000 mg/L = 100,000 ppm

## Slide 14: Chlorine Dosage
A concentration represented as a weight/volume
Expressed as mg/L or ppm
Most operators record pounds/day or gallons/day. This is the FEED RATE, not the dosage.
DOSAGE = DEMAND + RESIDUAL
Demand
Residual
Dosage

## Slide 15: Chlorine Demand
The amount of chlorine consumed or bound up by material in the water (expressed as mg/L)
This chlorine is NOT available as residual (free or total)
DOSAGE = DEMAND + RESIDUAL

## Slide 16: Chlorine Residual
The amount of chlorine remaining after the chlorine demand is satisfied (expressed as mg/L)
This chlorine IS available for further disinfection
DOSAGE = DEMAND + RESIDUAL

## Slide 17: Chlorine Residual
Combined
Three types of residuals
  Free
  Combined
  Total
TOTAL = COMBINED + FREE
Free
Total

## Slide 18
DOSAGE = DEMAND + RESIDUAL
DEMAND = DOSAGE – RESIDUAL
RESIDUAL = DOSAGE – DEMAND

## Slide 19: Calculate chlorine dosage if the demand is 0.35 mg/L and the residual is 0.82 mg/L.
1
(A) -0.47 mg/L
(B) 0.47 mg/L
(C) 1.17 mg/L
(D) 2.34 mg/L

## Slide 20: Calculate chlorine dosage if the demand is 0.35 mg/L and the residual is 0.82 mg/L.
(A) -0.47 mg/L
(B) 0.47 mg/L
(C) 1.17 mg/L
(D) 2.34 mg/L
1
Demand = 0.35 mg/L
Residual = 0.82 mg/L
Step 2: Make sure units match.
Step 3: Plug in the known values for Demand and Residual.
Dosage = 0.35 mg/L + 0.82 mg/L
Step 4: Solve.
Dosage = 0.35 mg/L + 0.82 mg/L = 1.17 mg/L
✓
✓
✓
✓
Step 1: Set up the equation to solve for the unknown, Dosage.
✓
✓

## Slide 21: Calculate chlorine dosage if the demand is 0.35 mg/L and the residual is 0.82 mg/L.
(A) -0.47 mg/L
(B) 0.47 mg/L
(C) 1.17 mg/L
(D) 2.34 mg/L
Chlorine Dosage = 1.17 mg/L
1
= 1.17 mg/L
Step 3: Plug in the known values for demand and residual.
Dosage = 0.35 mg/L + 0.82 mg/L
Step 4: Solve.
Dosage = 0.35 mg/L + 0.82 mg/L
Step 2: Make sure units match.
Step 1: Set up the equation to solve for the unknown, Dosage.

## Slide 22: Calculate Chlorine Residual
Calculate the residual chlorine if the demand is 2.0 mg/L and the dosage is 2.8 mg/L.
Demand = 2.0 mg/L
Dosage = 2.8 mg/L
2

## Slide 23
Step 1: Set up the equation to solve for the unknown, Residual.
Dosage = Demand + Residual
Calculate the residual chlorine if the demand is 2.0 mg/L and the dosage is 2.8 mg/L.
Demand = 2.0 mg/L
Dosage = 2.8 mg/L
Calculate Chlorine Residual
-Demand
-Demand
Residual = Dosage - Demand
Step 2: Make sure units match.
✓
✓
✓
✓
2

## Slide 24
Step 4: Solve.
Residual = 2.8 mg/L - 2.0 mg/L = 0.8 mg/L
Calculate the residual chlorine if the demand is 2.0 mg/L and the dosage is 2.8 mg/L.
Demand = 2.0 mg/L
Dosage = 2.8 mg/L
Calculate Chlorine Residual
Step 3: Plug in values for Dosage and Demand.
Residual = 2.8 mg/L - 2.0 mg/L
2

## Slide 25
Step 4: Solve.
Residual = 2.8 mg/L - 2.0 mg/L = 0.8 mg/L
Calculate the residual chlorine if the demand is 2.0 mg/L and the dosage is 2.8 mg/L.
Calculate Chlorine Residual
Residual chlorine = 0.8 mg/L
Step 3: Plug in values for Dosage and Demand.
Residual = 2.8 mg/L - 2.0 mg/L
1

## Slide 26: Specific Gravity

## Slide 27: Specific Gravity
Standard is usually:
  Water for a liquid or solid
  Air for a gas
= 1
= Unitless Number

## Slide 28: Specific Gravity
Some liquids are:
  Lighter than water
  Heavier than water
Chlorine solutions are heavier than water

## Slide 29: Specific Gravity
Specific gravity can be measured with a hydrometer
Specific gravity can also be calculated

## Slide 30
Specific Weight

## Slide 31
Specific Weight

## Slide 32
Specific Weight

## Slide 33
Specific Weight

## Slide 34
Specific Weight

## Slide 35: Specific Gravity
Specific gravity can be measured with a hydrometer
Specific gravity can also be calculated

## Slide 36: What is the specific gravity for a solution that weighs 10.27 lb/gal?
Step 1: Set up the equation to solve for the unknown, Specific Gravity.
(A) 0.81
(B) 1.23
(C) 1.93
(D) 18.61
3
Step 2: Make sure units match.
Specific Weight = 10.27 lb/gal
Step 3: Plug in the value for Specific Weight and solve.
✓
✓
✓
✓

## Slide 37: What is the specific gravity for a solution that weighs 10.27 lb/gal?
Step 3: Plug in the value for Specific Weight of a Substance and solve.
Step 2: Make sure units match.
1.23 is the specific gravity of a solution that weighs 10.27 lb/gal.
3
(A) 0.81
(B) 1.23
(C) 1.93
(D) 18.61
Step 1: Set up the equation to solve for the unknown, Specific Gravity.

## Slide 38: A 12.5% chlorine solution has a specific gravity of 1.20. How many pounds would 55 gallons of this solution weigh?
4

## Slide 39: A 12.5% chlorine solution has a specific gravity of 1.20. How many pounds would 55 gallons of this solution weigh?
4
Step 1: Set up the equation to solve for the unknown, Specific Weight. Multiply both sides by 8.34 lb/gal.
Specific Gravity = 1.20
Volume = 55 gal

## Slide 40: A 12.5% chlorine solution has a specific gravity of 1.20. How many pounds would 55 gallons of this solution weigh?
4
How many pounds
Specific Gravity = 1.20
Step 2: Make sure units match.
Volume = 55 gal
✓
✓
Step 3: Plug in the value for Specific Gravity and solve.

## Slide 41: A 12.5% chlorine solution has a specific gravity of 1.20. How many pounds would 55 gallons of this solution weigh?
x
4
Step 4: Calculate the weight of 55 gals of the solution by multiplying the specific weight of the solution by the volume of the solution.
Specific Gravity = 1.20
Volume = 55 gal
✓
✓

## Slide 42: A 12.5% chlorine solution has a specific gravity of 1.20. How many pounds would 55 gallons of this solution weigh?
x
45
Step 4: Calculate the weight of 55 gals of the solution by multiplying the specific weight of the solution by the volume of the solution.
550 lb is the weight of 55 gallons of 12.5% chlorine solution.

## Slide 43: The 50% sodium hydroxide solution you use to increase pH has a specific gravity of 1.50 at 20°C. How many pounds would 20 gallons of this solution weigh?
(A) 3.6 lbs
(B) 197 lbs
(C) 250 lbs
(D) 550 lbs
5
Specific Gravity = 1.50
Volume = 20 gal
Step 1: Set up the equation to solve for the unknown, Specific Weight. Multiply both sides by 8.34 lb/gal.
Step 3: Plug in the value for Specific Gravity and solve for Specific Weight.
Step 2: Make sure units match.
✓
✓

## Slide 44: The 50% sodium hydroxide solution you use to increase pH has a specific gravity of 1.50 at 20°C. How many pounds would 20 gallons of this solution weigh?
x (20 gal)
(A) 3.6 lbs
(B) 197 lbs
(C) 250 lbs
(D) 550 lbs
5
= 250 lb
Specific Gravity = 1.50
Volume = 20 gal
Step 4: Calculate the weight of 20 gals of the solution by multiplying the specific weight of the solution by the volume of the solution.

## Slide 45: The 50% sodium hydroxide solution you use to increase pH has a specific gravity of 1.50 at 20°C. How many pounds would 20 gallons of this solution weigh?
(A) 3.6 lbs
(B) 197 lbs
(C) 250 lbs
(D) 550 lbs
250 lb is the weight of 20 gallons of 50% sodium hydroxide solution.
5
Step 4: Calculate the weight of 20 gals of the solution by multiplying the specific weight of the solution by the volume of the solution.
x (20 gal)
= 250 lb

## Slide 46: The NaOCl in your day tank is getting a bit old and you want to determine its percent concentration. You weigh a gallon of it and your scale reads 9.08 lbs. What is your percent concentration?
% Concentration | Specific Gravity
1.0 | 1.020
2.0 | 1.034
3.0 | 1.048
4.0 | 1.062
5.0 | 1.076
6.0 | 1.089
7.0 | 1.103
8.0 | 1.116
9.0 | 1.129
10.0 | 1.142
11.0 | 1.155
12.0 | 1.168
13.0 | 1.181
14.0 | 1.193
15.0 | 1.206
Source: USA Bluebook Operator’s Companion
*values vary with temperature
6
Specific Weight = 9.08 lb/gal
Step 3: Plug in the value for Specific Weight and solve.
Step 1: Set up the equation to solve for the unknown, Specific Gravity.
Step 2: Make sure units match.
✓
✓
✓
✓

## Slide 47: The NaOCl in your day tank is getting a bit old and you want to determine its percent concentration. You weigh a gallon of it and your scale reads 9.08 lbs. What is your percent concentration?
% Concentration | Specific Gravity
1.0 | 1.020
2.0 | 1.034
3.0 | 1.048
4.0 | 1.062
5.0 | 1.076
6.0 | 1.089
7.0 | 1.103
8.0 | 1.116
9.0 | 1.129
10.0 | 1.142
11.0 | 1.155
12.0 | 1.168
13.0 | 1.181
14.0 | 1.193
15.0 | 1.206
Source: USA Bluebook Operator’s Companion
*values vary with temperature
6
Specific Weight = 9.08 lb/gal
Step 4: Read the chart to get the Percent Concentration value.

## Slide 48: The NaOCl in your day tank is getting a bit old and you want to determine its percent concentration. You weigh a gallon of it and your scale reads 9.08 lbs. What is your percent concentration?
% Concentration | Specific Gravity
1.0 | 1.020
2.0 | 1.034
3.0 | 1.048
4.0 | 1.062
5.0 | 1.076
6.0 | 1.089
7.0 | 1.103
8.0 | 1.116
9.0 | 1.129
10.0 | 1.142
11.0 | 1.155
12.0 | 1.168
13.0 | 1.181
14.0 | 1.193
15.0 | 1.206
Source: USA Bluebook Operator’s Companion
*values vary with temperature
6
fishersci.com
Percent concentration of NaOCl ≈ 6.0%
Step 4: Read the chart to get the Percent Concentration value.

## Slide 49: Feed Rate
Chlorine

## Slide 50: Chlorine/Chemical Purity
Gas Chlorine
100% Purity
Solid Chlorine
Calcium Hypochlorite
60-65% Purity
Liquid Chlorine
Sodium Hypochlorite
10-12% Purity
1% = 10,000 mg/L = 10,000 ppm

## Slide 51: In what situations at a water system does the feed rate formula come in handy for using chlorine?
Disinfecting Drinking Water
Shocking Wells
Batch Chlorinating Stored Water
Shocking Distribution Repairs/New Construction

## Slide 52: Feed Rate
The amount of chemical in pounds or gallons that you feed into a volume of water over a period of time.
Pounds/Day or Gallons/Day

## Slide 53: Feed Rate Equation Parts
Dosage, (mg/L) = The total amount of chemical solution fed into a volume of water.
Flow (MGD) = The volume of water in Million Gallons per Day that you are feeding the chemical into.
8.34 lb/gal = The weight of water. This is what converts gallons to pounds.
Purity, % expressed as a decimal = Purity of the chemical that you are feeding into the water expressed as a decimal.

## Slide 54: Feed Rate in Gallons per Day
gallons

## Slide 55: Feed (Not Feed Rate) in Pounds
Volume, MG

## Slide 56: Feed (Not Feed Rate) in Gallons
Volume, MG
gallons

## Slide 57: Pie Wheel Formulas
Top half: One side of the equation
Bottom half: Opposite side of the equation
Balance the top of the wheel, to the bottom of the wheel
**Your units must match the units in the pie wheel!!**

## Slide 58: How many pounds of 60% calcium hypochlorite is needed to add to a system each day that has a flow rate of 1.5 MGD to achieve a dosage of 1.1 mg/L?
Purity = 60%
Dosage = 1.1 mg/L
Flow Rate = 1.5 MGD
Step 1: Set up the equation to isolate the unknown, Feed Rate.
7
Step 2: Make sure units match.
Step 3: Plug in values for Dosage, Flow, and Purity and solve for Feed Rate.
✓
✓
✓
✓
✓
✓
✓
✓
= 0.60
100%

## Slide 59: How many pounds of 60% calcium hypochlorite is needed to add to a system each day that has a flow rate of 1.5 MGD to achieve a dosage of 1.1 mg/L?
22.9 lb of calcium hypochlorite must be added to the system each day to achieve a dosage of 1.1 mg/L.
7
Step 1: Set up the equation to isolate the unknown, Feed Rate.
Step 2: Make sure units match.
Step 3: Plug in values for dosage, flow, and purity and solve for feed rate.

## Slide 60
mg/L = parts per million
or

## Slide 61
A 500,000 gpd system has switched from gas disinfection to disinfection with a 10% sodium hypochlorite solution. How many gallons per day of 10% sodium hypochlorite are required to treat the water to a dosage of 2.8 mg/L?
Purity = 10%
Dosage = 2.8 mg/L
Flow = 500,000 gpd
8

## Slide 62
A 500,000 gpd system has switched from gas disinfection to disinfection with a 10% sodium hypochlorite solution. How many gallons per day of 10% sodium hypochlorite are required to treat the water to a dosage of 2.8 mg/L?
Flow = 500,000 gpd
8
= 0.10
Step 1: Rewrite the equation to solve for Feed in gallons/day.
Purity = 10%
Dosage = 2.8 mg/L
gallons
✓
✓

## Slide 63
A 500,000 gpd system has switched from gas disinfection to disinfection with a 10% sodium hypochlorite solution. How many gallons per day of 10% sodium hypochlorite are required to treat the water to a dosage of 2.8 mg/L?
Flow = 500,000 gpd
8
= 0.5 MGD
= 0.10
Step 2: Make sure units match.
✓
✓
✓
✓
1,000,000
✓
100%
✓
Purity = 10%
Dosage = 2.8 mg/L

## Slide 64
A 500,000 gpd system has switched from gas disinfection to disinfection with a 10% sodium hypochlorite solution. How many gallons per day of 10% sodium hypochlorite are required to treat the water to a dosage of 2.8 mg/L?
Purity = 10%
Dosage = 2.8 mg/L
Flow = 500,000 gpd
8
= 0.5 MGD
= 0.10
Step 1: Set up the equation to isolate the unknown, Feed Rate.
Step 2: Make sure units match.
Step 3: Plug in values for Dosage, Flow, and Purity and solve for Feed Rate.
= 14.00 gal/day

## Slide 65
A 500,000 gpd system has switched from gas disinfection to disinfection with a 10% sodium hypochlorite solution. How many gallons per day of 10% sodium hypochlorite are required to treat the water to a dosage of 2.8 mg/L?
8
14.00 gal/day of 10% sodium hypochlorite are required to treat 500,000 gallons of water per day to a chlorine dosage of 2.8 mg/L
= 14.00 gal/day

## Slide 66
How many gallons of 10% sodium hypochlorite are required to disinfect the water in a 20 ft diameter tank with 30 ft of water to a dosage of 5.0 mg/L?
9
Volume
Step 1: Rewrite the equation to solve for Feed in gallons.
gallons

## Slide 67
How many gallons of 10% sodium hypochlorite are required to disinfect the water in a 20 ft diameter tank with 30 ft of water to a dosage of 5.0 mg/L?
Dosage = 5.0 mg/L
Volume of Water =
Purity = 10%
Water Height = 30’
9
Tank Diameter = 20’
?
Step 2: Find the volume of our water in MG.
Volume of a Cylinder

## Slide 68
9
Volume of a Cylinder = πr2 x Height
Step 2: Find the volume of our water in MG.
Volume of a Cylinder = (0.785)(Diameter)2(Height)
How many gallons of 10% sodium hypochlorite are required to disinfect the water in a 20 ft diameter tank with 30 ft of water to a dosage of 5.0 mg/L?

## Slide 69
Tank Radius = 10’
Water Height = 30’
9
Tank Diameter = 20’
Step 2: Find the volume of our water in MG.
Volume of a Cylinder = πr2 x Height
units must be compatible
Step 3: Set up the equation to solve for the unknown, Volume of a Cylinder.
✓
✓
Step 4: Make sure units match.
✓
✓
2
How many gallons of 10% sodium hypochlorite are required to disinfect the water in a 20 ft diameter tank with 30 ft of water to a dosage of 5.0 mg/L?

## Slide 70
9
Volume of a Cylinder = πr2 x Height
units must be compatible
Step 5: Plug in values for Radius and Height and solve for Volume of Water.
= 9,425 ft3
Step 6: Convert ft3 to gallons.
Step 7: Convert gallons to MG.
Step 2: Find the volume of our water in MG.
Water Height = 30’
Tank Radius = 10’
How many gallons of 10% sodium hypochlorite are required to disinfect the water in a 20 ft diameter tank with 30 ft of water to a dosage of 5.0 mg/L?

## Slide 71
Dosage = 5.0 mg/L
Volume of Water = 0.075 MG
Purity = 10%
9
Step 8: Make sure units match.
✓
✓
✓
✓
= 0.10
✓
✓
Step 9: Plug values for Dosage, Volume, and Purity into the equation and solve for Feed in gallons.
= 3.75 gallons
How many gallons of 10% sodium hypochlorite are required to disinfect the water in a 20 ft diameter tank with 30 ft of water to a dosage of 5.0 mg/L?

## Slide 72
9
Step 8: Make sure units match.
Step 9: Plug values for Dosage, Volume, and Purity into the equation and solve for Feed in gallons.
= 3.75 gallons
3.75 gallons of 10% sodium hypochlorite are required to disinfect the tank to a chlorine dosage of 5.0 mg/L
How many gallons of 10% sodium hypochlorite are required to disinfect the water in a 20 ft diameter tank with 30 ft of water to a dosage of 5.0 mg/L?

## Slide 73
CONTACT INFORMATION
Department of Civil Engineering MSC01 1070
1 University of New Mexico
Albuquerque, NM 87131
swefctribal@unm.edu
http://swefc.unm.edu
Michelle Olson: meolson@unm.edu