## Slide 1
12/4/25
US Territories Water Operator Training Series
Session 12: Surface Water Treatment 1: Coagulation, Flocculation, Sedimentation
www.efcnetwork.org
This program is made possible under a cooperative agreement with US EPA.

## Slide 2: Tucker Colvin Research Scientist tcovin@unm.edu

## Slide 3
This training series is funded by the US EPA

## Slide 5: Schedule for 2025:
Links to recordings and material are available on our website at https://swefc.unm.edu/home/op-cert-trainings/
Date | Topic
6/26/25 | Program Overview, Test Format, Study & Test Tips
7/10/25 | Drinking Water System Overview - (Source, Treatment, & Distribution)
7/24/25 | Basic Operator Math (+, -, /, x, Exponents and basic algebra)
8/7/25 | Applied Operator Math (e.g. Areas, Volume, Flow Rates, Detention Time, Pressure/Hydraulic Head)
8/21/25 | Drinking Water Regulations
9/4/25 | Source Water Characteristics
9/18/25 | Surface Water Intake Components, Well Components, and O&M
10/2/25 | Disinfection 1: Chloramines, UV, Chlorine Dioxide, Chlorine
10/16/25 | Disinfection 2: Chlorine Disinfection Application for Sodium Hypochlorite and Gas Chlorine (including storage and safety)
10/30/25 | Disinfection 3: Distribution System Application, Residual Measurement, Evaluation & Adjustment,
11/13/25 | Disinfection 4: Chlorine Disinfection Math
12/4/25 | Surface Water Treatment 1: Coagulation, Flocculation, Sedimentation (including chemistry, process controls, operations)
12/18/25 | Surface Water Treatment 2: Filtration

## Slide 6: Schedule for 2026:
Links to recordings and material are available on our website at https://swefc.unm.edu/home/op-cert-trainings/
Date | Topic
1/21/2026 | Alternative Treatment Processes (e.g. flouridation, ion exhange, RO…)
2/4/2026 | Drinking Water Treatment Math & Concept Review
2/18/2026 | Safety Program Basics (including personal safety, equipment safety, facility safety)
3/4/2026 | Lead & Copper Rule, Corrosion Control
3/18/2026 | Distribution Systems 1: Hydraulics, Pipe Types, Selection, Installation, and Water Quality
4/1/2026 | Distribution Systems 2: Valves, Hydrants, Meters, and Service Connections
4/15/2026 | Distribution Systems 3: Storage and Booster Pumping
4/29/2026 | O&M: Pumps, Main, and Appurtenance Maintenance (including pressure monitoring, valve exercising, and flushing)
5/13/2026 | O&M: Cross Connection Control
5/27/2026 | O&M: Distribution System Math and Concept Review
6/10/2026 | Sampling & Lab Procedures/Analysis/Interpretation
6/24/2026 | Management Overview (including organization, communication, PR & record keeping)
7/8/2026 | Drinking Water Practice Exam and Review

## Slide 7: https://swefc.unm.edu/home/op-cert-trainings/

## Slide 8: Sign in for every session to ensure you get credit for attending

## Slide 9: Today’s Agenda
CT
Distribution System Application
Residual Measurement
Residual Evaluation
Dosage Adjustment
Repairing Mains

## Slide 10: Surface Water Treatment 1: Coagulation, Flocculation, Sedimentation
Turbidity reduction
Removal of suspended solids (TSS)
Removal of dissolved solids (TDS)
Removal or inactivation of organisms and viruses
Alter water chemistry
Purpose of treatment

## Slide 11: Log removal
1 log removal = 90%
2 log removal = 99%
3 log removal = 99.9%
4 log removal = 99.99%
Etc.
Cryptosporidium
Giardia
Bacteria
Viruses
Credits for treatment methods

## Slide 12: Surface water treatment steps
Intake / bar screening
Chemical addition
Rapid mix
Coagulation
Flocculation
Sedimentation
Filtration
pH adjustment / corrosion control
Disinfection
Fluoridation
Storage / distribution
Grit removal

## Slide 13: Pretreatment - chemical and physical process
Physical process – particle settling
Chemical process – creating particles to settle

## Slide 14: Colloids
Hydrophobic (water fearing)
Hydrophilic (water loving)
- Do not settle quickly due to small size - Charge overcomes force of gravity

## Slide 15: Surface water treatment steps
Intake / bar screening
Chemical addition
Rapid mix
Coagulation
Flocculation
Sedimentation
Filtration
pH adjustment / corrosion control
Disinfection
Fluoridation
Storage / distribution
Grit removal

## Slide 16: Surface water treatment steps
Intake / bar screening
Chemical addition
Rapid mix
Coagulation
Flocculation
Sedimentation
Grit removal
Filtration
pH adjustment
Disinfection
Fluorination

## Slide 17: Influent / grit removal

## Slide 18: Grit Removal Devices: Vortex Separator
Click on link to watch Video (Grit King) https://www.youtube.com/watch?v=v9Shzp4S1NU
Notes: Viortex
May have a grit pump or other mechanism at the bottom to extract the grit that accumulates at the bottom
These ware typically used where there is a lot of fine grit, and can remove up to about 73% or grit down to 0.004 inches in diameter (about a 10th of a millimeter)
These also have consistent m removal efficiencies over wide flow ranges and don’t have any moving parts. They have low head loss and usually have a small footprint – much smaller than a settling basin
Some of the downsides of vortex units is that they can have clogs in the grit sumps (down at the bottom), they’re typically proprietary
Ideally you would have two so you have redundancy for repairs or unexpected higher flows but a small plant probably won’t be able to afford it.

## Slide 19: Water Pre-treatment Chemicals
  Oxidants
  pH adjustment
  Coagulants
  Adsorption

## Slide 20
  Oxidizing agents include
  Chlorine
  Ozone
  Aeration
  Hydrogen peroxide
  Sodium permanganate
Water Pre-treatment Chemicals

## Slide 21: Water Pre-treatment Chemicals
  Oxidizing agents
  Precipitate out contaminants such as iron and manganese
  Decreased volatile organic compounds (VOCs), disinfection byproducts, hydrogen sulfide, carbon dioxide
  Can help with coagulation
  Neutralizes negative particle charges

## Slide 22: Water Pre-treatment Chemicals
  Coagulants

## Slide 23: Coagulation
Chemical process
Sediment particles are mostly negatively charged and push away from each other
Coagulant is positively charged and bonds to sediment to neutralize charge
Microflocs are formed
Notes: Photo credit: AWWA, https://www.youtube.com/watch?v=GVCWwWCLY7w

## Slide 24: Coagulation and Polymers/Polyelectrolytes
String-like chain molecules with charges along the string
Aid in coagulation (sometimes as primary coagulant)
Three types (type use depends on colloidal material)
  Cationic polymers – positive charged
  Anionic polymers – negative charged
  Nonionic polymers – not charged

## Slide 25: Factors that Affect Coagulation
pH
Alkalinity
Turbidity
Temperature
Polymer type
-

## Slide 26: Determining Chemical Dosage (jar test)
Notes: Source unknown

## Slide 27: Feed Rate
The amount of chemical in pounds or gallons that you feed into a volume of water over a period of time.
pounds or gallons/day

## Slide 28: Feed Rate Equation Parts
Dosage, (mg/L) = The total amount of chemical solution fed into a volume of water.
Flow (MGD) = The volume of water in Million Gallons per Day that you are feeding the chemical into.
8.34 lb/gal = The weight of water.
Purity, % expressed as a decimal = Purity of the chemical that you are feeding into the water expressed as a decimal.

## Slide 29: 1) After doing a jar test, a 500K gpd water plant determined they want a dosage of 1.3 mg/L of their alum liquid solution with a 48% concentration. What is their lbs per day of alum solution usage?
Feed Rate, lb/day =
Feed Rate, lb/day =
Feed Rate, lb/day =
A) 5.42 lb/day
B) 11.3 lb/day
C) 86.9 lb/day
D)112.9 lb/day

## Slide 30: Solubility of Salts and Water Treatment
Salt = metal + other mineral
Some salts soluble in water and some are not
Most undesirable minerals in water are soluble salts
Add chemicals and adjust pH to make soluble undesirables insoluble so can be removed

## Slide 31: Pretreatment Equipment - Chemical Feeders
Volumetric (most common)
  Auger feeders
  Positive displacement metering pumps
Notes: Peristaltic pump
Solenoid piston pump

## Slide 32: Pretreatment Equipment - Chemical Feeders
Gravimetric
  Conveyor with set of scales to maintain constant weight of materials on belt
  Not used much in water treatment because most chemicals are corrosive and will damage the scale mechanism

## Slide 33: Rapid Mix
Rapid mixers
In-line mixers
Static mixers
Aeration
Source: Ozone Solutions

## Slide 34: Coagulation (flash/rapid mix)
The process of decreasing the stability of the colloids in water using salts
Makes particles sticky
Mechanical mixers
Detention time of 1-3 minutes
Mixing velocities = 5-7 ft/sec

## Slide 35: Flocculation
Occurs in large basin
Physical process
Microflocs bump together to create larger flocs

## Slide 36: Flocculation
Mixing to increase flocs impacts, but not to break apart flocs
Too slow of mixing can result in settling in floc basin

## Slide 37: Flocculation Equipment

## Slide 38: Sedimentation
Large basin with long detention time
Sedimentation can be assisted by plate or tube settlers
Mechanism at bottom to remove sludge

## Slide 39: Circular Sedimentation Basin

## Slide 40: Up-Flow Clarifiers/Solids Contact Basin
Combine coagulation, flocculation, and sedimentation into one unit

## Slide 41: 2) Find the detention time in hours for a sedimentation basin that is 295 ft long, 80.0 ft wide, and with a water depth of 11.0 ft. Flow is 1.50 MGD
A) 1.29 hours
B) 4.15 hours
C) 31.0 hours
D) 69.8 hours

## Slide 42: Next time:
Links to recordings and material are available on our website at https://swefc.unm.edu/home/op-cert-trainings/
Date | Topic
6/26/25 | Program Overview, Test Format, Study & Test Tips
7/10/25 | Drinking Water System Overview - (Source, Treatment, & Distribution)
7/24/25 | Basic Operator Math (+, -, /, x, Exponents and basic algebra)
8/7/25 | Applied Operator Math (e.g. Areas, Volume, Flow Rates, Detention Time, Pressure/Hydraulic Head)
8/21/25 | Drinking Water Regulations
9/4/25 | Source Water Characteristics
9/18/25 | Surface Water Intake Components, Well Components, and O&M
10/2/25 | Disinfection 1: Chloramines, UV, Chlorine Dioxide, Chlorine
10/16/25 | Disinfection 2: Chlorine Disinfection Application for Sodium Hypochlorite and Gas Chlorine (including storage and safety)
10/30/25 | Disinfection 3: Distribution System Application, Residual Measurement, Evaluation & Adjustment,
11/13/25 | Disinfection 4: Chlorine Disinfection Math
12/4/25 | Surface Water Treatment 1: Coagulation, Flocculation, Sedimentation (including chemistry, process controls, operations)
12/18/25 | Surface Water Treatment 2: Filtration

## Slide 43
CONTACT INFORMATION
Department of Civil Engineering MSC01 1070
1 University of New Mexico
Albuquerque, NM 87131
505-277-0644
swefc@unm.edu
http://swefc.unm.edu
SW EFC email: swefc@unm.edu