## Slide 1
2/5/2026
US Territories Water Operator Training Series
Session 15: Drinking Water Treatment Math
www.efcnetwork.org
This program is made possible under a cooperative agreement with US EPA.

## Slide 2: Matt Ziegler Program Director
Your trainer for today

## Slide 3
This training series is funded by the US EPA

## Slide 5: Schedule for 2026:
Links to recordings and material are available on our website at https://swefc.unm.edu/home/op-cert-trainings/
Date | Topic
1/22/26 | Alternative Treatment Processes (e.g. flouridation, ion exhange, RO…)
2/5/26 | Drinking Water Treatment Math & Concept Review
2/19/26 | Safety Program Basics (including personal safety, equipment safety, facility safety)
3/5/26 | Lead & Copper Rule, Corrosion Control
3/19/26 | Distribution Systems 1: Hydraulics, Pipe Types, Selection, Installation, and Water Quality
4/2/26 | Distribution Systems 2: Valves, Hydrants, Meters, and Service Connections
4/16/26 | Distribution Systems 3: Storage and Booster Pumping
4/30/26 | O&M: Pumps, Main, and Appurtenance Maintenance (including pressure monitoring, valve exercising, and flushing)
5/14/26 | O&M: Cross Connection Control
5/28/26 | O&M: Distribution System Math and Concept Review
6/11/26 | Sampling & Lab Procedures/Analysis/Interpretation
6/25/26 | Management Overview (including organization, communication, PR & record keeping)
7/9/26 | Drinking Water Practice Exam and Review

## Slide 6: https://swefc.unm.edu/home/op-cert-trainings/

## Slide 7: Sign in for every session to ensure you get credit for attending

## Slide 8: Feed Rate
Chemicals That Are Not Chlorine

## Slide 9: How many pounds per day of alum, is needed to treat 8.2 MGD to a dosage of 12 mg/L? The purity of the alum is 49%.
Example
Dosage = 12 mg/L
Flow rate = 8.2 MGD
Purity = 49% = 0.49
Feed Rate, lb/day =
1,675 pounds/day of 49% alum are required to treat 8.2 MGD to a dosage of 12 mg/L.

## Slide 10: If 16.34 lbs/day of zinc orthophosphate has been fed into a 1 MGD water system, determine the average dose in mg/L.
Practice
Feed rate = 16.34 lb/day
Flow rate = 1.0 MGD
Purity = 100% = 1
2.0 mg/L is the average dose of zinc orthophosphate when 1 MGD of water is treated with 16.34 lbs/day.
1

## Slide 11: Surface Area Application of Chemicals

## Slide 12: Copper sulfate is used for algae control. Your reservoir is 1,200 ft long and 600 ft wide. At an application rate of 5.5 lb per surface acre, how much copper sulfate is required?
Example
Reservoir length = 1,200’
Reservoir width = 600’
Application rate = 5.5 lb/acre
91 lbs of copper sulfate are needed to treat a 1,200’ x 600’ reservoir at an application rate of 5.5 lb per surface acre.
No Equation on Formula Sheet

## Slide 13: Filter Loading Rate

## Slide 14: Filter Loading Rate
Also known as the Filtration Rate.
Measured in gpm/ft2.
Allows comparison of actual conditions with design specifications.

## Slide 15: A filter has a surface area of 920 sq ft. What is the filtration rate in gallons per minute per square foot, if it receives a flow of 4,875 gpm?
Example
Filter surface area = 920 ft2
Flow = 4,875 gpm
5.3 gpm/ft2 is the filtration rate for this filter at a flow rate of 4,875 gpm.

## Slide 16: A filter has a surface area of 350 sq ft. What is the filtration rate in gallons per minute per square foot, if it receives a flow of 1,200 gpm?
Practice
Filter surface area = 350 ft2
Flow = 1,200 gpm
3.4 gpm/ft2 is the filtration rate for this filter at a flow rate of 1,200 gpm.
2

## Slide 17: Surface Loading Rate

## Slide 18: Surface Loading Rate
The amount of water per day (gpd) passing over 1 square foot (ft2) of a treatment process.
Allows comparison of actual conditions with design specifications.
AKA – Surface Settling Rate or Surface Overflow Rate

## Slide 19: What is the surface loading rate for a circular clarifier that is 90 feet in diameter, if it is treating an instantaneous flow rate of 5 cfs?
Example
Clarifier = 90 ft diameter
Flow rate = 5 cfs
Need flow in gpd &
Need area in ft2

## Slide 20: What is the surface loading rate for a circular clarifier that is 90 feet in diameter, if it is treating an instantaneous flow rate of 5 cfs?
Example
Clarifier = 90 ft diameter (calculate area)
Flow rate = 5 cfs (convert to gpd)

## Slide 21: What is the surface loading rate for a circular clarifier that is 90 feet in diameter, if it is treating an instantaneous flow rate of 5 cfs?
Example
Clarifier area = 6,359 ft2
Flow rate = 3,230,000 gpd
508 gpd/ft2 is the surface loading rate for this circular clarifier at a flow rate of 5 cfs.

## Slide 22: A rectangular sedimentation basin measures 375 ft by 50 ft, what is the surface loading rate if it is treating an instantaneous flow rate of 17 cfs?
Practice
375 ft
50 ft
Sedimentation basin = 375 ft x 50 ft
Flow rate = 17 cfs
Need flow in gpd &
Need area in ft2

## Slide 23: A rectangular sedimentation basin measures 375 ft by 50 ft, what is the surface loading rate if it is treating an instantaneous flow rate of 17 cfs?
Practice
Sedimentation basin = 375 ft x 50 ft (calculate area)
Flow rate = 17 cfs (convert to gpd)
3
4

## Slide 24: A rectangular sedimentation basin measures 375 ft by 50 ft, what is the surface loading rate if it is treating an instantaneous flow rate of 17 cfs?
Practice
Sedimentation basin area = 18,750 ft2
Flow rate = 10,982,000 gpd
586 gpd/ft2 is the surface loading rate for this sedimentation basin at a flow rate of 17 cfs.
5

## Slide 25: Backwash Rate & Backwash Rise Rate

## Slide 26: Backwash Rate
Backwash rate is the movement of water in the opposite direction of filtration to clean and remove filtered solids.
Measured in gpm/ft2.
Allows comparison of actual conditions with design specifications.
No direct formula on the ABC formula sheet.
Can Adapt Formula

## Slide 27: A filter has an area of 840 sq ft with a backwash pumping rate of 20 cfs. What is the backwash rate in gallons per minute per square foot?
Example
Filter area = 840 ft2
Flow rate = 20 cfs
Need flow in gpm

## Slide 28: A filter has an area of 840 sq ft with a backwash pumping rate of 20 cfs. What is the backwash rate in gallons per minute per square foot?
Example
10.7 gpm/ft2 is the backwash rate for this filter at a flow of 20 cfs.
Filter area = 840 ft2
Flow rate = 8,976 gpm

## Slide 29: Based on your calculation of the filter backwash rate in Question Ex3, what is the filter backwash rise rate for this filter in inches/minute?
Example
Filter backwash rate = 10.7 gpm/ft2
17.2 in/min is the filter backwash rise rate for this filter if it is backwashed at a rate of 10.7 gpm/ft2.

## Slide 30: A filter has an area of 50 sq ft with a backwash pumping rate of 1.7 cfs. What is the backwash rate in gallons per minute per square foot?
Practice
Filter area = 50 ft2
Flow rate = 1.7 cfs
Need flow in gpm
6

## Slide 31: A filter has an area of 50 sq ft with a backwash pumping rate of 1.7 cfs. What is the backwash rate in gallons per minute per square foot?
Practice
15.3 gpm/ft2 is the backwash rate for this filter at a flow of 1.7 cfs.
Filter area = 50 ft2
Flow rate = 763 gpm
7

## Slide 32: Based on your calculation of the filter backwash rate in Question 7, what is the filter backwash rise rate for this filter in inches/minute?
Practice
Filter backwash rate = 15.3 gpm/ft2
24.5 in/min is the filter backwash rise rate for this filter if it is backwashed at a rate of 15.3 gpm/ft2.
8

## Slide 33: Percent Removal
%

## Slide 34: Percent Removal
The amount of a contaminant removed in percent form.
Helps determine if meet some SDWA regulatory requirements.
Helps inform if treatment plant is doing its job.
Allows comparison of actual conditions with design specifications.

## Slide 35: The iron content of a raw water is 1.81mg/L. What is the percent removal if the finished water contains 0.11 mg/L iron?
Example
Raw water iron (In) = 1.81 mg/L
Finished water iron (Out) = 0.11 mg/L
94% is the percent removal of iron in the finished water.

## Slide 36: You operate a surface water treatment plant and one of the SDWA requirements as part of the DBPR is to remove a certain percentage of Total Organic Carbon. If your raw water TOC is 3.2 mg/L and your finished water TOC is 0.9 mg/L, calculate the percent removal for TOC.
Practice
Raw water TOC (In) = 3.2 mg/L
Finished water TOC (Out) = 0.9 mg/L
72% is the percent removal of TOC in the finished water.
9

## Slide 37: Ordering Treatment Material

## Slide 38: It is time to submit an order so that you can do a maintenance on your filter to keep it operating and removing contaminants. You must add 8 inches of coal to one of the 12 ft by 8 ft filters in your treatment plant. If each bag holds 3.5 ft3, how many bags do you need to order?
Example
Height of coal = 8 inches
Filter Size = 12 ft x 8 ft
Bag size = 3.5 ft3
Need to determine volume of coal adding to filter in ft3
19 bags of coal should be ordered to add 8 inches to the filter.

## Slide 39: Next time:
Links to recordings and material are available on our website at https://swefc.unm.edu/home/op-cert-trainings/
Date | Topic
1/22/26 | Alternative Treatment Processes (e.g. flouridation, ion exhange, RO…)
2/5/26 | Drinking Water Treatment Math & Concept Review
2/19/26 | Safety Program Basics (including personal safety, equipment safety, facility safety)
3/5/26 | Lead & Copper Rule, Corrosion Control
3/19/26 | Distribution Systems 1: Hydraulics, Pipe Types, Selection, Installation, and Water Quality
4/2/26 | Distribution Systems 2: Valves, Hydrants, Meters, and Service Connections
4/16/26 | Distribution Systems 3: Storage and Booster Pumping
4/30/26 | O&M: Pumps, Main, and Appurtenance Maintenance (including pressure monitoring, valve exercising, and flushing)
5/14/26 | O&M: Cross Connection Control
5/28/26 | O&M: Distribution System Math and Concept Review
6/11/26 | Sampling & Lab Procedures/Analysis/Interpretation
6/25/26 | Management Overview (including organization, communication, PR & record keeping)
7/9/26 | Drinking Water Practice Exam and Review

## Slide 40
CONTACT INFORMATION
Department of Civil Engineering MSC01 1070
1 University of New Mexico
Albuquerque, NM 87131
505-277-0644
swefc@unm.edu
http://swefc.unm.edu
SW EFC email: swefc@unm.edu