## Slide 1
03/03/2026
US Territories Wastewater Operator Training Series
Session 17: Wastewater Math Part 3 – Flow, Detention Time and Loading
www.efcnetwork.org
This program is made possible under a cooperative agreement with US EPA.
Notes: Welcome to all of our participants from CNMI, Guam and American Samoa to session 17 in our wastewater operator training series. Today we will be focusing on calculating flow, detention time and loading.

## Slide 2: Your trainers for today:
Dawn Nall
Project Director
Valeria Cortes-Mora
Professional Intern

## Slide 3
This training series is funded by the EPA

## Slide 5: WPI/ABC Operator Certification
Notes: This series is designed to supplement and reinforce the ABC Need to Know Criteria for the Wastewater Operator level 1 and 2 exams though there will be some higher level topics covered, and we won’t always follow the exact order listed in the NTKs
https://www.gowpi.org/services/abc-testing/standardized-exams/standardized-wastewater-treatment-operator-exams/

## Slide 6: Use all your resources
Notes: All the information we’ve covered and more is in these books – those happen to be my personal copies that I consult on the regular.

## Slide 7: Schedule for 2026:
Date | Topic
1/20/26 | Concept and Math Review Session
2/3/26 | Disinfection Part 1 (chlorination/dechlorination) + related math
2/17/26 | Disinfection Part 2 - UV and other methods
3/3/26 | WW Math Part 3 (Flow, Detention Time)
3/17/26 | WW Math Part 4 (BOD Math /Advanced WW Math)
3/31/26 | Solids Handling Part 1 (Mechanical Solids Separation)
4/14/26 | Solids Handling Part 2 (Solids Handling)
4/28/26 | Sampling
5/12/26 | Regulations (NPDES Permits and Discharge Limitations)
5/26/26 | Treatment System Maintenance
6/9/26 | Lab Procedures/Analysis/Interpretation or alternate topic
6/23/26 | Using Technology in daily operations (SCADA, Computer, Tablets, CMMS, AI, etc.)
7/7/26 | Course Review Session - Short sample exam?
Notes: 26 sessions total
1 hour each
This is the schedule for the remainder of this year,
The trainers will vary depending on the topic
We’re now on session 15

## Slide 8: https://swefc.unm.edu/home/op-cert-trainings/
Notes: The sessions are all being posted to our website so that you can go back and review them. I checked today and all of the sessions are posted, and this session should be posted in a day or two.

## Slide 9: Sign in for every session to ensure you get credit for attending
Notes: Be sure to sign in if you are attending in a group. The facilitator at your location will forward these to us and we will keep track of your attendance hours for credits;
With that lets get to today’s content!

## Slide 10
Overview
Velocity
Flow Rates
Detention Times
Loading Rates
Practice problems
  Pencil and paper needed
  ABC Formula Sheet helpful
    https://gowpi.org/services/abc-testing/formula-conversion-tables/
Notes: Today we are going to be discussing the formulas that you use to calculate velocity, flow rate, detention time and loading rates. I will provide time for you to practice each type of problem, so have a pencil and paper handy and if you can, pull up a copy of the ABC Formula Sheet.

## Slide 11: Velocity and Flow Rates
How Fast and How Much
OR
Speed and Volume

## Slide 12: Velocity vs Flow rates
Velocity = ft/sec
Flow = ft3/sec
Velocity: How fast water flows through a pipe in a given time; How far something travels in a given amount of time.
Feet per second (ft/s)
Meters per sec (m/s)
Flow: Volume of water flowing through a pipe in a given time.
Gallons per minute (gpm)
Cubic feet per second (ft3/sec)
Million gallons per day (MGD)

## Slide 13: Velocity
You put a rubber ducky at the beginning of a pipe that is 520 feet long. It comes out the end in 142 seconds. How fast is water flowing through your pipe?
(assuming water is flowing the same speed as the ducky)
5
(A) 378 ft/sec
(B) 73,840 ft/sec
(C) 0.28 ft/sec
(D) 3.7 ft/sec
V = distance / time
V =
V = 3.7 ft/sec

## Slide 14: Velocity vs Flow rates
Velocity = ft/sec
Flow = ft3/sec
Velocity: How fast water flows through a pipe in a given time; How far something travels in a given amount of time.
Feet per second (ft/s)
Meters per sec (m/s)
Flow: Volume of water flowing through a pipe in a given time.
Gallons per minute (gpm)
Cubic feet per second (ft3/sec)
Million gallons per day (MGD)

## Slide 15: Flow
Your flow meter for your lift station pump is broken, but you want to figure out the pump's capacity. You open up the blow off and fill up 5-gallon buckets. You fill up 8 buckets in one minute. What is the capacity of your pump in GPM?
7
(A) 13 gal/min
(B) 40 gal/min
(C) 400 gal/min
(D) 130 gal/min
Flow = volume / time
Flow = 40 gal / minute
5 gallon

## Slide 16: Flow
What is the flow in gpm in an 18-inch diameter line when your rubber ducky is moving through it at a velocity of 2.5 ft/sec?
Flow = Velocity x Area
4.42 ft3
Flow = 2.5 ft/sec x 1.77 ft2
Conversion factors:
7.48 gallons = 1 ft3
60 secs = 1 min
Diameter = 18”
sec
60 sec
1 min
7.48 gals
1 ft3
=1984 gpm
V = 2.5 ft/sec
D= 18”
Flow = 4.42 ft3/sec
Diameter = 18”/12 = 1.5 ft
Area = 3.14 * r2
Area = 3.14 * (0.75 ft)2
Area = 3.14 * 0.56 ft2
Area = 1.77 ft2
Radius = 1.5 ft/2 = 0.75 ft

## Slide 17: Flow – you try it
What is the flow in gpm in a 12-inch diameter line when your rubber ducky is moving through it at a velocity of 1.1 ft/sec?
Flow = Velocity x Area
0.864 ft3
Flow = 1.1 ft/sec x 0.785 ft2
Conversion factors:
7.48 gallons = 1 ft3
60 secs = 1 min
Diameter = 12”
sec
60 sec
1 min
7.48 gals
1 ft3
= 388 gpm
V = 1.1 ft/sec
D= 12”
Flow = 0.864 ft3/sec
Diameter = 12”/12 = 1 ft
Area = 3.14 * r2
Area = 3.14 * (0.5 ft)2
Area = 3.14 * 0.25 ft2
Area = 0.785 ft2
Radius = 1 ft/2 = 0.5 ft
(A) 388 gal/min
(B) 9,293 gal/min
(C) 775 gal/min
(D) 1984 gal/min
8

## Slide 18: Detention Time

## Slide 19: Detention Time
The time water stays in a given reservoir or treatment process.

## Slide 20: Your secondary clarifier is 40 ft in diameter and 25 ft deep. Your max daily flow is 1.2 MGD. To determine if your clarifier meets the recommended detention time, you need to calculate the detention time of the clarifier in hours.
40ft
25ft
9
Diameter = 40 ft
Radius = 40 ft/2 = 20 ft
(A) 1 day
(B) 4.7 hours
(C) .20 days
(D) .20 hours
= 234,872 gal
Volume = π * r2 * Height
Volume = 3.14 * (20 ft)2 * 25 ft
Volume = 3.14 * 400 ft2 * 25 ft
Volume = 31,400 ft3
=4.7 hours
> 2-3 recommended design DT

## Slide 21
4 Clarifiers = 40’ x 30’ x 21‘
Find the detention time in hours for the following WWTP: • 4 rectangular clarifiers each 40.0 ft long, 30.0 ft wide, and with an average water depth of 21.00 ft. • 1 oxidation ditch 295 ft long, 80.0 ft wide, and with a water depth of 11.0 ft. • Flow is 3.50 MGD

## Slide 22: Find the detention time in hours for the following WWTP: • 4 rectangular clarifiers each 40.0 ft long, 30.0 ft wide, and with an average water depth of 21.00 ft. • 1 oxidation ditch 295 ft long, 80.0 ft wide, and with a water depth of 11.0 ft. • Flow is 3.50 MGD
1 Oxidation Ditch = 295’ x 80’ x 11‘

## Slide 23
Vol of Oxidation Ditch = 1,942,000 gals
Vol of Clarifiers = 753,984 gals
Find the detention time in hours for the following WWTP: • 4 rectangular clarifiers each 40.0 ft long, 30.0 ft wide, and with an average water depth of 21.00 ft. • 1 oxidation ditch 295 ft long, 80.0 ft wide, and with a water depth of 11.0 ft. • Flow is 3.50 MGD

## Slide 24
Vol of WWTP = V = 2.7 MG
Flow = Q = 3.5 MGD
18.5 hours is the detention time for treatment in the WWTP.
Find the detention time in hours for the following WWTP: • 4 rectangular clarifiers each 40.0 ft long, 30.0 ft wide, and with an average water depth of 21.00 ft. • 1 oxidation ditch 295 ft long, 80.0 ft wide, and with a water depth of 11.0 ft. • Flow is 3.50 MGD

## Slide 25: Detention Time Rearranged
A circular clarifier is being designed to accommodate an average flow of 76,250 gpd. To accommodate the space restrictions of the plant the diameter of the clarifier must not exceed 13 feet. What must the designed depth be to achieve a detention time of 2.5 hours?

## Slide 26: Your Turn – Practice Detention Time
A rectangular sedimentation basin is 75 feet long, 30 feet wide, and 20 feet deep. If the treatment plant has a daily flow rate of 2.25 million gallons per day (MGD), what is the detention time in hours?
What do we know?
Dimensions: 75 (L), 30 (W), 20 (D)
Flow Rate: 2.25 MGD
What are we looking for?
Detention Time in hours
What do we need?
Equations:
DT = Volume/Flow
Volume = LxWxD
Conversions:
1ft3 = 7.48 gallons
Step 1: Calculate the volume of the basin
Volume = length x width x depth
Volume = 75 ft x 30 ft x 20 ft
Volume = 45,000 ft3
Step 2: Convert volume from ft3 to gallons
45,000 ft3 x 7.48 gallons = 336,600 gallons
Step 3: Calculate Detention Time
DT = Volume/Flow
DT = 336,600 gal / 2,250,000 gallons per day
DT = 0.1496 days
1ft3
Step 4: Convert to hours
0.1496 days x 24 hours
3.6 hours
1 day

## Slide 27: Weir Loading Rate
Measures the amount of water leaving a settling tank per linear unit of length of weir per day
Used to ensure weirs are not hydraulically overloaded, efficient sedimentation is occurring, and solids do not infiltrate clarifier effluent
Recommended 10,000-20,000 gpd/ft (124,100-248,200 Lpd/m)
Typically correlates with a correct detention time
**Use “weir” as indicator that weir length is involved**

## Slide 28: Weir Loading Rate Example
The flow for a circular clarifier is 1.2 MGD with a 26-foot diameter. What is the weir overflow rate in gallons per foot of weir length per day?

## Slide 29: Weir Loading Rate Practice 1
A rectangular sedimentation tank with a length of 12 ft, a width of 18 ft, and a depth of 11 ft has a flow of 190,000 gpd. What is the weir overflow rate of this this sedimentation tank if influent enters on one wide side of the tank and effluent exits on the other?
18 ft
12 ft

## Slide 30: Surface Loading Rate
Measures the amount of water passing over a unit of surface area per day
Another parameter that indicates clarifiers are not hydraulically overloaded and has a direct relationship to the settleable solids removal efficiency of sedimentation tanks
Recommended 300-1,200 gpd/ (12,160-48,645 Lpd/)
**Use “surface” as indicator that surface area is involved**

## Slide 31: Surface Loading Rate Example
What is the surface loading rate of a circular clarifier with a depth of 8.0 ft, a diameter of 9.0 ft and an effluent flow of 42,000 gpd?

## Slide 32: Surface Loading Rate Practice
Known design parameters for a rectangular clarifier are listed below. What is the surface loading rate in gal/ft2*day? What is the depth required to maintain a maximum detention time of 3.0 hours?
Knowns:
Q= 2.2 MGD
L= 72 ft
W= 28 ft

## Slide 33
Questions?

## Slide 34
CONTACT INFORMATION
Department of Civil Engineering MSC01 1070
1 University of New Mexico
Albuquerque, NM 87131
505-277-0644
swefc@unm.edu
http://swefc.unm.edu
swefc@unm.edu