## Slide 1
03/17/2026
US Territories Wastewater Operator Training Series
Session 18: Wastewater Math Part 4 – Advanced Wastewater Math
www.efcnetwork.org
This program is made possible under a cooperative agreement with US EPA.
Notes: Welcome to all of our participants from CNMI, Guam and American Samoa to session 17 in our wastewater operator training series. Today we will be focusing on calculating flow, detention time and loading.

## Slide 2: Your trainers for today:
A.J. Barney
Research Engineer
Valeria Cortes-Mora
Professional Intern

## Slide 3
This training series is funded by the EPA

## Slide 5: WPI/ABC Operator Certification
Notes: This series is designed to supplement and reinforce the ABC Need to Know Criteria for the Wastewater Operator level 1 and 2 exams though there will be some higher level topics covered, and we won’t always follow the exact order listed in the NTKs
https://www.gowpi.org/services/abc-testing/standardized-exams/standardized-wastewater-treatment-operator-exams/

## Slide 6: Use all your resources

## Slide 7: Schedule for 2025:
Date | Topic
1/20/26 | Concept and Math Review Session
2/3/26 | Disinfection Part 1 (chlorination/dechlorination) + related math
2/17/26 | Disinfection Part 2 - UV and other methods
3/3/26 | WW Math Part 3 (Flow, Detention Time)
3/17/26 | WW Math Part 4 (BOD Math /Advanced WW Math)
3/31/26 | Solids Handling Part 1 (Mechanical Solids Separation)
4/14/26 | Solids Handling Part 2 (Solids Handling)
4/28/26 | Sampling
5/12/26 | Regulations (NPDES Permits and Discharge Limitations)
5/26/26 | Treatment System Maintenance
6/9/26 | Lab Procedures/Analysis/Interpretation or alternate topic
6/23/26 | Using Technology in daily operations (SCADA, Computer, Tablets, CMMS, AI, etc.)
7/7/26 | Course Review Session - Short sample exam?
Notes: 26 sessions total
1 hour each
This is the schedule for the remainder of this year,
The trainers will vary depending on the topic
We’re now on session 15

## Slide 8: https://swefc.unm.edu/home/op-cert-trainings/
Notes: The sessions are all being posted to our website so that you can go back and review them. I checked yesterday and all of the sessions 1-9 are posted, and this session should be posted in a day or two.

## Slide 9: Sign in for every session to ensure you get credit for attending
Notes: Be sure to sign in if you are attending in a group. The facilitator at your location will forward these to us and we will keep track of your attendance hours for credits;
With that lets get to today’s content!

## Slide 10: Who am I?? A.J Barney- Environmental Engineer, Biologist, NM Certified WW Operator
Notes: 11 SWEFC Team members

## Slide 11: BOD
Notes: 60 Min
Likely 45 Minutes
SVI, F:M, MCRT/SRT, Return Sludge Rate
Optional Recirc Rates etc.

## Slide 12: Biochemical Oxygen Demand (BOD)
Analytical measure of the organic strength of wastewater
Amount of dissolved oxygen (DO) consumed by microbes
Expressed as (mg/L)
Incubated for 5-days at 20°C
BOD used to evaluate wastewater treatment plant (WWTP) processes
BOD indicates process efficiency
BOD indicates the impact of WWTP discharge on the environment
NPDES parameter
Notes: The first thing we’ll review in this training is biochemical oxygen demand or BOD for short.
BOD is commonly referred to as the organic strength of wastewater
and is one of our core targets for removal through wastewater treatment along with solids, pathogens, ammonia and nitrogen
Now the definition of biochemical oxygen demand is that it is the analytical measure of the amount of oxygen consumed during the decomposition of organic material.
Specifically measures the amount of dissolved oxygen consumed by aerobic microorganisms in 1 L of wastewater
Expressed as and measured in mg/L
Samples are incubated for 5-days at 20°C
BOD aids in evaluating wastewater treatment plant and processes performance
Applies to all biological processes
BOD levels indicate the efficiency of organic pollutants removal
BOD levels help anticipate impact treated wastewater may have on the environment
Used as design parameter for plants to meet NPDES permit requirements
The first thing we’ll review in this training is biochemical oxygen demand or BOD for short.
BOD is commonly referred to as the organic strength of wastewater
and is one of our core targets for removal through wastewater treatment along with solids, pathogens, ammonia and nitrogen
Now the definition of biochemical oxygen demand is that it is the analytical measure of the amount of oxygen consumed during the decomposition of organic material.
Specifically measures the amount of dissolved oxygen consumed by aerobic microorganisms in 1 L of wastewater
Expressed as BOD_5 and measured in mg/L
Samples are incubated for 5-days at 20°C
BOD aids in evaluating wastewater treatment plant and processes performance
Applies to all biological processes
BOD levels indicate the efficiency of organic pollutants removal
BOD levels help anticipate impact treated wastewater may have on the environment
Used as design parameter for plants to meet NPDES permit requirements

## Slide 13: Loading Rate
The rate at which chemicals are added to wastewater or discharged in effluent
Measured in lbs/day or kg/day
Referred to as feed rate as well
mg/L=ppm
Notes: For application to wastewater treatment, BOD loading refers to the rate at which mostly organics and some other pollutants are introduced to wastewater.

## Slide 14: BOD Units
BOD is measured in mg/L
=ppm=1mg/L
Notes: Real quick I want to expand on that concept that 1 mg/L is = to 1 ppm
We demonstrate this by first explaining that 1 Liter of water is = to 1 kg
So if we perform a unit conversion on a mg/L using the fact that 1 kg of anything is also equal to 1,000,000 mg
So we
I keep reiterating this concept, because I think it’s very important to get in the habit of cancelling our units, which is a good practice to ensure you performed your calculations in the correct order.

## Slide 15: BOD Loading Example
Samples were taken at the influent of a WWTP and a test was performed. The average influent of the WWTP is 1 MGD and the sample analysis determined that the BOD concentration for that day was 240 mg/L. Calculated the BOD loading to this WWTP.
Notes: Notice in the first term of my bracket I have my MG on the top and my days on the bottom, but I didn’t do that to my second term.
This is because I’m gong to cancel out the mg/L.
This is not always intuitive, but the more you practice understanding what these math problems want and how to find it in word problems the more you can be familiar with how to save yourself some time adjusting your mathematical operations and doing things like cancelling out terms easier. The only way I know how to do this for most people is lots of practice.

## Slide 16: BOD Loading Practice
You work at a WWTP with a primary clarifier and a tricking filter and want to determine the current organic loading to your process, but first you need to calculate the BOD loading to the trickling filter. You collect a sample of the primary effluent and determine the average BOD is 129 mg/L. The flow to the trickling filter is 0.04 MGD. What is the average BOD loading to the trickling filter in lbs/day?
Notes: Poll 1
40,000 gpd
43 lbs/day
This is a longer form than usual. We’ll leave this survey up and wait for a decent amount of the group to respond, but while we work this out if anyone is stuck please turn on your mic or ask for some clarification through the chat. This goes for all of today’s polls.

## Slide 17: Organic Loading Rate
Measured the amount of organic material (expressed in BOD) applied to a treatment system per unit of media (volume or surface area) per day
Used as a design parameter to ensure regulatory compliance
Performance monitoring indicator
Applies to: Trickling Filter
RBCs
Lagoons
Expressed in lbs BOD/1,000 /day and kg BOD//day
Expressed in lbs BOD/1,000 /day and kg BOD//day

## Slide 18: Organic Loading Rate Equations
Rotating Biological Contactors
Trickling Filters

## Slide 19: Process Control Calculations
Notes: 60 Min
Likely 45 Minutes
SVI, F:M, MCRT/SRT, Return Sludge Rate
Optional Recirc Rates etc.

## Slide 20: F:M Ratio
Represents the ratio of organic material (food) to the amount of microorganisms in a bioreactor
BOD concentration represents the food
MLVSS concentration represents the microorganisms
Monitoring the F:M ratio is essential to ensure that bioreactors are treating wastewater correctly and permit requirements are met
Low F:M ratios limit microbial populations and decrease wastewater treatment
High F:M ratios lead to excessive sludge production
The F:M ratio inversely correlates with the SRT/MCRT
Notes: Represents the amount of organic material (food) entering a bioreactor compared to the mass of microorganisms available to consume the organic material
BOD concentration represents the food in the reactor
And MLVSS concentration represents the microorganisms in the reactor
Monitoring the F:M ratio is essential to ensure that bioreactors are treating wastewater correctly and permit requirements are met
Low F:M ratios limit microbial populations and decrease wastewater treatment
High F:M ratios lead to excessive sludge production, which can lead to treatment issues and contribute unwanted solids
The F:M ratio inversely correlates with the SRT/MCRT

## Slide 21: F:M Ratio Equation
Q = Flow Rate into aeration Tank
BOD = concentration of BOD in the flow into Aeration Tank
Vab = volume of Aeration Tank
MLSS = concentration of suspended solids in the Aeration Tank
MLVSS (or VSS) = concentration of MLVSS in the Aeration Tank
Units are (lb BOD/lb VSS/day or kg BOD/kg VSS/day)
Units sometimes represents as just per day
Ideal F:M ratio is 0.2-0.6 lb BOD/lb VSS/day
Notes: V
Mixed liquor suspended solids
Mixed liquor volatile suspended solids
We don’t always know what the MLVSS is.
In the field you can collect sample and during analysis the lab will volatize the MLSS solids to determine the MLVSS concentration
But in the testing environment this should be provided.
MLVSS is usually 60-80% of the MLSS

## Slide 22: F/M Ratio Units
=
Notes: These calculations seem a little complicated because we’re dealing with a lot of different units. BOD and MLSS are going to be measured in mg/L. but flow will typically be in gallons or MG/day and tank volume will also be in Gal or MG.
As you can see here the equation resembles that BOD loading right off the bat, but it seems like the unit conversion is more complicated. I think this is a little extra work for no reason, but it is notable since it is how the F/M equation is presented in the sacremento guide.
I honestly don’t know why they do this, because it is the same thing as 8.34 lbs/ gal but with more steps.
The Liter over milligrams is the reciprocal to ppm and just cancels the million in the million gallon or MG.
And in the rest of the equation everything cancels out. The MG at top and bottom and mg/L at the top and bottom.
You can do the math using the conversion factors, but you’ll have the same factors it the top and bottom of the fraction so they cancel out and all we’re left with is days.
The end result is expressed as lbs/lbs, or kg/kg or ton over ton – we’re just using lbs here because it’s the most common unit we’ll see in the US, but that tends not to matter as those units canel out.
And really really what we get is a unitless ratio per day.
Finally this is what the equation looks like in our most common formula sheet associated with ABC testing

## Slide 23: F:M Ratio Example
A small wastewater treatment plant has the following data:
BOD = 260 mg/L
Biomass = 75% of solids
Tank Volume (Vab) = 84,000 gal
Flow (Q) = 136,000 gpd
MLSS = 1,900 mg/L
What is the F:M ratio for this plant?
1) Calculate MLVSS:
Notes: point out gallon and MG

## Slide 24: F:M Ratio Practice Problem
The following data was collected for the performance of an activated sludge plant. What is the F:M ratio for this plant?
BOD = 250 mg/L
Biomass = 80% of solids
Tank Volume = 0.9 MG
Flow = 3.2 MGD
MLSS = 3,100 mg/L
1) Calculate MLVSS:
Notes: 3.2 MGD
The numerator
2,480 mg/L
0.36

## Slide 25: Sludge Age
Indicates the average amount of time that microorganisms or solids spend in the activated sludge process
Ensures correct types of microbes are present and wastewater treatment is optimized
Operator certification tests and plant operations typically utilize more specific variants
Solids Retention Time
Minimum Cell Retention Time

## Slide 26: SRT vs MCRT
Some certifications treat these interchangeably, but some provide slightly different equations
Sac State course uses SRT
ABC Testing Formula/ Conversion Table treats them interchangeably
MCRT equations sometimes do not include the TSSs in the secondary clarifier or only account for living solids
Activated sludge process with ONLY BOD removal, have an SRT range of 1-5 days

## Slide 27: SRT Equation Adjustments
No TSS for secondary clarifiers
Solids are immediately pumped from the secondary clarifier
Solids in effluent are considered negligible

## Slide 28: SRT Example 1
Given the following data for an activated sludge process, calculate the SRT.
Aeration Basin Volume | Vab | 0.9 MG
Secondary Clarifier Volume | Vsc | 0.5 MG
Influent Flow | Q | 3.6 MGD
Waste Sludge Flow | QWAS | 0.14 MGD
Mixed Liquor Suspended Solids | MLSS | 3200 mg/L
Waste Sludge Suspended Solids | TSSWAS | 7000 mg/L
Final Effluent Suspended Solids | TSSeff | 9 mg/L
Secondary Clarifier Suspended Solids | TSSsc | 540 mg/L

## Slide 29: SRT Example 2
You have been asked to calculate the MCRT of a small wastewater treatment plant with an average daily flow of 1,000,000 GPD. You are given design specifications for the plant, which indicates that the volume of the aeration tank is 380,000 gallons, and the volume of the secondary clarifier is 95,000 gallons. You run some analysis to find the remaining values needed to calculate the MCRT for the plant. Using the treatment parameters provided below, calculate the MCRT for the plant and identify if this is in the desired range for a conventional activated sludge treatment plant:

## Slide 30: Sludge Wasting
Process by which excess biomass or MLSS is remove from activated sludge processes
Referred to as waste activated sludge (WAS)
Variable that can be manipulated most readily to adjust F:M ratio and sludge age, MCRT and SRT
There is limited control of influent, effluent, and their associated biomass or MLSS once the processes are operating
The pumping of solids from the secondary clarifier can be adjusted easily
Rearrange SRT equation to calculate WAS rate:

## Slide 31: Sludge Wasting Rate Example
Data was collected for a conventional activated sludge plant that is experiencing decreased treatment efficiency and is provided below. To decrease the sludge age of the microbial population in the the plant manager would like to decrease the SRT to 6 days to more closely resemble the design specifications. What should the target sludge wasting rate be to accomplish this?
Aeration Basin Volume | Vab | 0.60 MG
Secondary Clarifier Volume | Vsc | 0.22 MG
Influent Flow | Q | 1.9 MGD
Waste Sludge Flow | QWAS | 29,000 gpd
Mixed Liquor Suspended Solids | MLSS | 3600 mg/L
Waste Sludge Suspended Solids | TSSWAS | 6600 mg/L
Final Effluent Suspended Solids | TSSeff | 14 mg/L

## Slide 32: Sludge Wasting Rate Example Cont’d
SRT = 6 days
Answer= 0.0705 MGD = 70,500 gpd
Tripling the wasting rate would be too drastic, and it is likely you would want to increase slower over a couple days.
Aeration Basin Volume | Vab | 0.60 MG
Secondary Clarifier Volume | Vsc | 0.22 MG
Influent Flow | Q | 1.9 MGD
Waste Sludge Flow | QWAS | 29,000 gpd
Mixed Liquor Suspended Solids | MLSS | 3600 mg/L
Waste Sludge Suspended Solids | TSSWAS | 6600 mg/L
Final Effluent Suspended Solids | TSSeff | 14 mg/L
Notes: What do we use for the effluent flow if it isn’t explicitly given?
What is .60 MG in gal
What is .22 MG in gal
What is 1.9 MGD in gpd

## Slide 33: Sludge Wasting Rate Practice
Data was collected for a conventional activated sludge plant that is experiencing decreased treatment efficiency and is provided below. To decrease the sludge age of the microbial population in the the plant manager would like to decrease the SRT to 7 days to more closely resemble the design specifications. What should the target sludge wasting rate be to accomplish this?
Aeration Basin Volume | Vab | 0.60 MG
Secondary Clarifier Volume | Vsc | 0.22 MG
Influent Flow | Q | 2.0 MGD
Waste Sludge Flow | QWAS | 29,000 gpd
Mixed Liquor Suspended Solids | MLSS | 2400 mg/L
Waste Sludge Suspended Solids | TSSWAS | 12000 mg/L
Final Effluent Suspended Solids | TSSeff | 9 mg/L

## Slide 34: Sludge Wasting Rate Practice
SRT = 7 days
Answer= 0.0336 MGD = 33,600 gpd
Tripling the wasting rate would be too drastic, and it is likely you would want to increase slower over a couple days.
Aeration Basin Volume | Vab | 0.60 MG
Secondary Clarifier Volume | Vsc | 0.22 MG
Influent Flow | Q | 2.0 MGD
Waste Sludge Flow | QWAS | 29,000 gpd
Mixed Liquor Suspended Solids | MLSS | 2400 mg/L
Waste Sludge Suspended Solids | TSSWAS | 12000 mg/L
Final Effluent Suspended Solids | TSSeff | 9 mg/L
Notes: 1.9 MGD
600,000 gal
33,600 gpd
0.029 gpd

## Slide 35: Sludge Volume Index (SVI)
SVI describes the settling of sludge
Measurement of the volume occupied by activated sludge after settling for 30 minutes
Tested in the lab using a settleability test
1-2 liters monitored in a beaker
The sample is allowed to sit for 30 minutes
Sludge volume recorded at 5 and 30 minutes
Notes: SVI is a parameter used to describe the settling characteristics of sludge in the activated sludge process
Measurement of the volume occupied by activated sludge after setline in the aeration tank for 30 minutes
Tested in the lab using a settleability test
1-2 liters of activated sludge sample is place in a wide-mouthed clear cylinder beaker with clear, visible volume indicators
The sample is allowed to sit for 30 minutes
Sludge volume measurements are recorded at 5 and 30 minutes

## Slide 36: SVI Example
An operator collecting his normal samples for an activated sludge plant places 1-L of mixed liquor in a wide mouth beaker. The MLSS concentration for this sample is 2600 mg/L and the sludge volume after 30-minutes was 390 mL. Calculate the SVI.

## Slide 37: SVI Practice
An operator collecting his normal samples for an activated sludge plant places 2-L of mixed liquor in a wide mouth beaker. The MLSS concentration for this sample is 2900 mg/L and the sludge volume after 30-minutes was 487 mL. Calculate the SVI.
Notes: 2 L
84 mL/g

## Slide 38: Final Thoughts
Practice!!!!!!
Become efficient with unit conversions
ALWAYS include units
Practice cancelling units

## Slide 39
Questions?

## Slide 40
CONTACT INFORMATION
Department of Civil Engineering MSC01 1070
1 University of New Mexico
Albuquerque, NM 87131
505-277-0644
swefc@unm.edu
http://swefc.unm.edu
A.J. Barney: ajbarney1@unm.edu

## Slide 41: Basic Math Refresher
Notes: 30 Min

## Slide 42: Need to know math concepts
Arithmetic (Addition, Subtraction, Multiplication, Division)
Order of operations (PEMDAS)
Basic algebra
Basic unit of measurements
Fractions, decimals, and percentages
Concentrations
Shapes
Area
Volume
Basic Statistics
Notes: Arithmetic (Addition, Subtraction, Multiplication, Division)
Fractions, decimals, and percentages
Order of operations (PEMDAS)
Basic algebra- Inequalities and variables
Shapes
Basic unit of measurements-Understanding units of measurement are important to understand what you are looking and scaling for in the field and in the classroom

## Slide 43: Order of Operations
P- Parentheses
E- Exponent
M- Multiplication
D- Division
A- Addition
S- Subtraction
Area of a Circle

## Slide 44: Order of Operations
P- Parentheses
E- Exponent
M- Multiplication
D- Division
A- Addition
S- Subtraction
Volume of a cylinder+ Dh

## Slide 45: Order of Operations
P- Parentheses
E- Exponent
M- Multiplication
D- Division
A- Addition
S- Subtraction
P

## Slide 46: Order of Operations
P- Parentheses
E- Exponent
M- Multiplication
D- Division
A- Addition
S- Subtraction
B

## Slide 47: Order of Operations
P- Parentheses
E- Exponent
M- Multiplication
D- Division
A- Addition
S- Subtraction
Surface Area of a Cone

## Slide 48: Basic Algebra
Understand:
Constants
Variables
How to identify the variables in a word problem
Ex. If your thermometer reads 100°C, what is the temperature in Fahrenheit?
Notes: To excel in wastewater math we need to understand a few basic algebra principles.
The first is constants
Constants are fixed problems in algebra problems that serve as a reference point to calculate the correct solution. As the name suggests these stay constant whenever you use the questions. They are represented by set values.
This is highlighted here in the equation to calculate Fahrenheit.
Then there are variables, which are represented by a symbol and in the basic equation represents an unknown value. Variables take on different values depending on the information we find for the problem we are solving.
So in our same example our Fahrenheit and Celsius symbols represent our variables, and as you can see since the answer varies it is also a variable.
The other important algebra skill we need is understanding how to identify what information is a variable that we can use to solve our problem.
For example in our same problem what exactly are we trying to solve for?
And what information is given to solive it?
Solve for F
And we are given C

## Slide 49: Units
Correct units ensure accuracy, consistency, correct communication, compliance, and safety in wastewater treatment
Common WW units:
Volume-
Flow-
Concentration-
Area-
Pressure-
Use units to determine if your answer makes sense!
Gallons (gal), Cubic Feet (), Liters (L), Cu. Meters ()
Million Gallons per Day (MGD), Gallons per Minute (gpm), Cubic Feet per Second (CFS)
Milligrams per Liter (mg/L), Parts per Million (ppm)
Square Feet (, Square Meters (, Acres
lbs per Square Inch (psi)
Notes: So expanding on the concepts of units.
Units are important for a variety of other reasons
Including they^^^
Common WW units are used as measurements in wastewater math

## Slide 50: Using Units to Identify Problem Solutions
Units can be used to solve word problems
Ex. If your thermometer reads 100°C, what is the temperature in Fahrenheit?
If you don’t know how to solve this problem you first try to identify a problem that includes the units we’re looking for.
Ex 2. An operator needs to determine the feed rate needed to provide a 10 mg/L chlorine dosage to a disinfection contact chamber. The operator knows that the average flow is 120,000 gpd and they are using a 13% strength solution of sodium chloride. What does the operator need to set the feed rate to in lbs/day?
Notes: Units can and SHOULD be used as a strategy to help you solve WW math problems
Lets use our previous problem for example.
Lets practice this
First what are we trying to find?
Referring to our formulas sheets, does anyone see an equation we can use?
Do we have all of the inputs w
The need for the equation?

## Slide 51: Using Units to Solve Wastewater Problems
Units can also be used to help identify the correct formula to use in wastewater problems
Ex. An operator needs to determine the feed rate needed to provide a 10 mg/L chlorine dosage to a disinfection contact chamber. The operator knows that the average flow is 120,000 gpd and they are using a 13% strength solution of sodium chloride. What does the operator need to set the feed rate to in lbs/day?
Notes: If your problem

## Slide 52: Fractions and Decimals
Used to represent parts of a whole
Units in the field are rarely whole numbers
Converting:
Fraction to decimals (divide the numerator by the denominator)
Ex.
Decimals to Fraction (write the decimal as a fraction, multiply the numerator and decimal by 100, simplify using the greatest common divisor.
Ex.

## Slide 53: Dividing by Fractions
Especially useful to understand unit conversions
When dividing by fractions the numerator and denominator trade place for the fraction we are dividing by
Then multiply by the reciprocal fraction
Ex.
Ex.
**Bottom of the bottom becomes the top!!**

## Slide 54: Units and Exponents
When adding units
Units don’t change
Units must be the same or compatible to add those variables together
Can add units that are different, but measure the same thing (i.e. volume)
Ex. Gallons and cubic feet () can be added together, but they require a unit conversion
Ex 2. Cubic feet and square feet () cannot be added, because they measure different things

## Slide 55: Units and Exponents
When multiplying units you add the exponents together
Ex.
When dividing units you subtract the exponent of the denominator from the numerator
Ex.

## Slide 56: Percentages
A way to express a number as a fraction of 100 using the percent symbol (%)
Intuitive way to demonstrate a ratio
In wastewater used to communicate removal efficiencies, concentrations, chemical dosages, resource recoveries, etc.

## Slide 57: Converting Percentages into Decimals
Remove the percentage sign
Divide the number by 100
Remove the percentage sign
Move decimal left two places
65%
= 65/100
= 0.65
65%
= 0.65

## Slide 58: Converting Decimals into Percentages
Multiply the decimal number by 100
Add the percentage sign
Move decimal right two places
Add the percent sign
0.65
= 0.65*100
= 65%
0.65
= 65%

## Slide 59: Concentrations
The amount of a substance suspended or dissolved in a liquid
Used to measure the following in wastewater:
Nutrient Levels
Pollutants Levels
Effluent Quality
Chemical Dosing
Calculated by dividing the mass of the target substance by the volume of the liquid it is in
Measured in mg/L, ppm, µg/L, ppb, g/, g/L
Understanding concentrations helps protect the public health and the environment

## Slide 60: Calculating Concentration
An ammonia standard is creating by adding .5 mg of ammonia to .2 L of ultrapure water. What is the ammonia concentration of this solution?
Notes: Ammonia typically NH4Cl

## Slide 61: Common Concentrations
TS
TSS
BOD
MLSS
MLVSS

## Slide 62: Shapes
Square
Rectangle
Triangle
Trapezoid
Circle
Cube
Rectangular Prism
Cylinder
Sphere
s
s
h
b
h
b
h
b
r
Circumference = πD
D
r
Notes: First we’ll start with shapes.
Wastewater processes come in all different shapes in sizes and it’s important to understand how to use them in wastewater calculations
These are the common shapes you’ll run into and they each have a different formula to calculate the area or volume.
For this slide we have a examples of the shapes you’ll see and how to calculate the areas for
Squares = side squared
Rectangle ””
Triangle “”
Circle “”
Then we will also need to the dimensions of the most common 3D shapes which are:
We’ll walk through solving some of these problems in just a little.

## Slide 63: Shapes
Square
Rectangle
Triangle
Trapezoid
Circle
Cube
Rectangular Prism
Cylinder
Sphere
r
Circumference = πD
r
Notes: First we’ll start with shapes.
Wastewater processes come in all different shapes in sizes and it’s important to understand how to use them in wastewater calculations
These are the common shapes you’ll run into and they each have a different formula to calculate the area or volume.
For this slide we have a examples of the shapes you’ll see and how to calculate the areas for
Squares = side squared
Rectangle ””
Triangle “”
Circle “”
Then we will also need to the dimensions of the most common 3D shapes which are:
We’ll walk through solving some of these problems in just a little.

## Slide 64: Shapes
Square
Rectangle
Triangle
Trapezoid
Circle
Cylinder
Cube
Rectangular Prism
Cylinder
Cone
s
s
h
b
h
b
h
b
r

## Slide 65: Surface Area
Area = Amount of space enclosed within a shapes boundaries
Measured in square units
Surface Area = Area of the surface of a 3D object
Surface Area of a Rectangle/ Square = L×W
Surface Area of a Circle =
h
b
r
Notes: Area measured the amount of space enclosed within the boundaries of a two dimensional shape.
Typically measured in square units

## Slide 66: VOLUMES
Water and other fluid substances take on the shape of their container
Tanks
Pipes
Excavations
Open reservoirs
Clarifiers
Jars of homemade salsa

## Slide 67
VOLUMES
Area of a rectangle = Length x Width
Area of a circle = π x r2
Volume of a rectangular Prism = Length x Width x Height
Length
Width
radius
Height
Height
radius
Volume of a Cylinder = π x r2 x Height
radius
Notes: Now volume measure the amount of space that an object takes up.
We explain volume by expanding on the concept of area.
For simple 3D objects that we use in wastewater calculations, we multiply our surface area by height.
It’s basically stacking up layers of the objects surface area up to the needed height.
For the volume of a rectangular prism which is the technical term for the shape of the rectangular tanks we use in wastewater operations.
As lon

## Slide 68
VOLUME OF A BOX
Volume of a rectangular prism = Length x Width x Height
Length 24 ft
Width 12 ft
Height 4 ft
Volume = Length x Width x Height
Volume = 24 ft x 12 ft x 4 ft
Volume = 1152 ft3
Example:

## Slide 69: Volume of a Rectangular Practice Problem
Find the volume of fill dirt in ft3 needed to replace an excavation that is 60 feet long, 3 feet wide, and 4 feet deep.
L = 60 ft
H = 4 ft
W = 3 ft
Vol = L x W x H
Vol =60 ft x 3 ft x 4 ft
Vol = 720 ft3
(A) 67 ft3
(B) 80 ft3
(C) 720 ft3
(D) 3460 ft3
2

## Slide 70
VOLUME OF A CYLINDER
Diameter 20 ft
Height 32 ft
Volume = π × r2 × Height
Volume = 3.14 × (10 ft)2 × 32 ft
Volume = 3.14 × 100 ft2 × 32 ft
Example:
Volume of a cylinder = π × r2 × Height
Volume of a cylinder = 0.785 × D2 × Height
Radius 10 ft
Volume = 10,048 ft3

## Slide 71: Volume of a Cylinder Practice Problem
What is the volume in cubic feet for a clarifier that is 15 feet tall and has a diameter of 18 feet?
D = 18 ft
(A) 424 ft3
(B) 3815 ft3
(C) 38,150 ft3
(D) 179,776 ft3
4
R = 9 ft
H = 15 ft
Volume = π * r2 * Height
Volume = 3.14 * (9 ft)2 * 15 ft
Volume = 3.14 * 81 ft2 * 15 ft
Volume = 3,815 ft3
Volume of a cylinder = π * r2 * Height

## Slide 72: Temperature
Many wastewater systems have temperature ranges they function in
Motors and pumps
Microbiological activity operates best in the Mesophilic range (20-40°C or 68-104°F)
Chemical reactions
Equipment may report temperature in different unit
Notes: Motors and pumps must operate within a certain temperature range. Otherwise high temperatures may indicate something is wrong and can lead to issues.
Temperature changes call for operational changes in biological processes
Higher temperatures increase the reactions of most chemical reactions and certain compounds become more soluble at lower temperatures and can be settled out.
It’s important to understand what process can be manipulated with temperature changes or management.
Sometimes our equipment

## Slide 73: Temperature Practice Problems
An operator measures the temperature of a solution they are mixing and find that the temperature of their mixture is 212°F. What is the temperature of their mixture in degrees Celsius.
The temperature of a digester that operates in the mesophilic range is measured to be 37°C. What is this temperature in degrees Fahrenheit?
Notes: Motors and pumps must operate within a certain temperature range. Otherwise high temperatures may indicate something is wrong and can lead to issues.
Temperature changes call for operational changes in biological processes
Higher temperatures increase the reactions of most chemical reactions and certain compounds become more soluble at lower temperatures and can be settled out.
It’s important to understand what process can be manipulated with temperature changes or management.
Sometimes our equipment

## Slide 74: Significant Figures (Sig Figs)
Indicates the number of digits you should round your answer to for a calculated answer
Rule of thumb is to use the same number of digits as the variable with the least number of sig figs used in your calculation
Omit trailing 0s and initial 0s in a decimal.
Ex.
Ex. r=14 ft
**Unlikely to be on your test, test answers will not be overly precise, and wrong answers will not be incorrect based on sig figs**
Sig Figs = 2

## Slide 75: Unit Conversions and Davidson Pie Wheel
Notes: 30 Min 6 practice questions

## Slide 76: Standard Unit Conversions
Process of changing one measurement unit to another
Min to Hours
Feet to Miles
Gallons to Liters
Requires a conversion factor
Calculated by lining up as fractions and multiplying across by the conversion factor
Unit conversions are required for standardization, simplification and to convert to the correct unit in many wastewater equations
Useful strategy for solving wastewater calculations

## Slide 77: Common Water Math Conversions
Percent solution strength to decimal percent
Time
  Seconds to minutes to hours to days
Lengths
  Inches to feet
  Feet to miles
Volumes
  Cubic feet (ft3) to gallons
  Gallons to million gallons
Velocity
  ft/s to mph
Flow
  gpm to MGD

## Slide 78: What is a conversion factor?
A numerical relationship used to when converting from one system of units to another
Ratio that expresses how many of one unit are equal to another
Formula Sheet

## Slide 79: How do we use conversion factors?
Multiple your measurement by the conversion factor
What you’re really doing:
Turning the conversion factor into a fraction
Multiplying by one
1 gal = 3.79 Liters = 1 = 1
You can multiply anything by 1 and not change its quantity, only change the units.
Goal is to identify units that cancel out and result in desired units
Notes: Unit conversions must be arranged correctly for units to

## Slide 80: Example of unit conversion
Your Sodium Hypochlorite tank holds 40 gallons, but the store sells it by the liter. How many liters of Sodium Hypochlorite do you need to fill up your 40-gallon tank?
1 gal = 3.79 liters
40 gal
1 1 gal
40 gal 3.79 L
= ~ 150 L
= ~ 150 L
Units lined up to cancel out

## Slide 81: Time Unit Conversion
Your well runs for 11.25 hours/day. How many minutes does it run in a day?
1 day 1 h
11.25 h 60 min
=
5 minutes
270 minutes
675 minutes
16,200 minutes

## Slide 82: Length Unit Conversion
You are trying to determine the volume of 1,000 feet of 8-inch pipe. The first thing you want to do is make your units match. How many feet in diameter is the 8” pipe?
1 12 in
8 in 1 foot
= 0.67 feet
0.67 feet
0.75 feet
9.6 feet
96 feet

## Slide 83: Volume Unit Conversion #1
Your storage tank holds 212,000 gallons of water, how many million gallons (MG) of water is in the tank?
1 1,000,000 gals
212,000 gals 1 MG
= 0.212 MG
0.00212 MG
0.0212 MG
0.212 MG
2.12 MG

## Slide 84: Volume Unit Conversion #2
To figure out the volume of your clarifier, you measure it with your tape measure and determine it holds 46 cubic feet of water. How many gallons does your clarifier hold?
1 1 ft3
46 ft3 7.48 gal
= 344 gal
6.1 gal
53 gal
344 gal
466 gal

## Slide 85: Volume Unit Conversion #3
Your storage tank is 40’ in diameter with 36’ of water in it. You calculated the total volume of water in the tank as 45,216 ft3. How many gallons of water are in the tank?
1 1 ft3
45,216 ft3 7.48 gal
= 338,216 gal
6,044 gal
60,440 gal
121,414 gal
338,216 gal

## Slide 86: Volume Unit Conversion #4
You dig a trench for a new pipeline and remove 6,800 ft3 of soil. To replace the soil removed, how many cubic yards (yd3) of fill do you need to order?
1 27 ft3
6,800 ft3 1 yd3
= 252 yd3
10 yd3
252 yd3
2,267 yd3
183,600 yd3
Not on Formula Sheet
1 ft x 1 ft x 1 ft = 1 1 yd x 1 yd x 1 yd = 1 1 yd = 3 ft
3 ft x 3 ft x 3ft = 27 = 1

## Slide 87: Volume Unit Practice:
How many cubic yards is 720 cubic feet?
L = 60 ft
D = 4 ft
W = 3 ft
1 yard = 3 feet
1 yd3 = 27 ft3
(A) 27 yd3
(B) 240 yd3
(C) 2160 yd3
(D) 19,440 yd3
You could now convert to dump truck loads if you wanted
3
= 26.7 yd3
Do you usually buy fill dirt in cubic feet? We need to convert to cubic yards!

## Slide 88
VOLUME OF A CYLINDER
Diameter 20 ft
Height 32 ft
Volume = π × r2 × Height
Volume = 3.14 × (10 ft)2 × 32 ft
Volume = 3.14 × 100 ft2 × 32 ft
Example:
Volume of a cylinder = π × r2 × Height
Volume of a cylinder = 0.785 × D2 × Height
Radius 10 ft
Volume = 10,048 ft3
Convert to gallons:
= 75,159 gal
≈ 75,000 gal

## Slide 89: Multiple Unit Conversion Practice Problem
A lift pump is rated to pump 245 m3/day of raw influent, how many gallons per minute can this pump manage?
= 45.0 gpm
= 45.0 gpm
day
3.785
1,440 min

## Slide 90: Davidson Pie Wheel
Many wastewater and water certification tests or classes provide this visual tool to simplify complex equations
The pie wheel is divided into sections that represent the variables used for different wastewater and water equations
The variables on the bottom of the pie wheel are multiplied to calculate the value of the variable in the top half of the pie wheel
Interchangeably dividing the value at the top of the pie by any of the variable in the bottom half will result in value for the other variables or product of the variable in the bottom half
Area of a Triangle
base
height
Feed Rate
(lbs./day)
Flow
(MGD)
Dose
(mg/L)
lbs./gal
Notes: Mention that the pie wheel may have variables written out in full or just be represented by a symbol

## Slide 91: Davidson Pie Wheel Example 1
Calculate the are of a triangle that was measured to have a base of 10 inches and a height of 6 inches.
10 in
6 in
b
h
Area of a Triangle
Area of a Triangle
Notes: Mention that the pie wheel may have variables written out in full or just be represented by a symbol

## Slide 92: Davidson Pie Wheel Example 2
To achieve the proper detention time an activated sludge plant is required to have a rectangular sludge basin with a volume of 168 It has been determined that the space available to house the tank has a length of 7 ft and a width of 8 ft. What height is needed to provide the desired tank volume?
7 ft
8 ft
168
l
w
h
h
Volume of a Rectangular Tank

## Slide 93: Davidson Pie Wheel Practice
A wastewater treatment plant (WWTP) requires a chlorine dosage of 12 mg/L to properly disinfect the wastewater before discharging. The WWTP has a daily flow of .125 MGD. Calculate the needed chlorine feed rate for the chlorinator with 100% pure chlorine to achieve the required chlorine dosage.
Feed Rate
(lbs./day)
Flow
(MGD)
Dose
(mg/L)
lbs./gal
436 lbs./day
12.51 lbs./day
2,267 gpm
18 mg/L

## Slide 94: Davidson Pie Wheel Practice
A wastewater treatment plant (WWTP) requires a chlorine dosage of 12 mg/L to properly disinfect the wastewater before discharging. The WWTP has a daily flow of 0.125 MGD. Calculate the needed chlorine feed rate for the chlorinator with 100% pure chlorine to achieve the required chlorine dosage.
12.51 lbs./day
Feed Rate
(lbs./day)
Flow
(MGD)
Dose
(mg/L)
lbs./gal
Feed Rate
(lbs./day)
0.125 MGD
12
mg/L
lbs./gal

## Slide 95: Benefits of Conversion Factors and Davidson Pie Wheels
Conversion Factors
Simplifies complex equations
Reduces calculation errors by cancelling out units and verifying results have the correct units
Davidson Pie Wheels
Simplifies complex equations
Increases efficiency of calculations
Provides additional tool to ensure accuracy
Notes: Speeds up the calculation process

## Slide 96: Velocity and Flow Rates
Notes: 30 Min 6
Likely 45 min and 8-10

## Slide 97: Velocity vs Flow rates
Velocity = ft/sec
Flow = ft3/sec
Velocity: How fast water flows through a pipe in a given time; How far something travels in a given amount of time.
- Feet per second (ft/s)
- Meters per sec (m/s)
Flow: Volume of water flowing through a pipe in a given time. AM
- Gallons per minute (gpm)
- Cubic feet per second (ft3/sec)
- Million gallons per day (MGD)

## Slide 98: Velocity
You put a rubber ducky at the beginning of a pipe that is 520 feet long. It comes out the end in 142 seconds. How fast is water flowing through your pipe?
(assuming water is flowing the same speed as the ducky)
5
(A) 378 ft/sec
(B) 73,840 ft/sec
(C) 0.28 ft/sec
(D) 3.7 ft/sec
V = distance / time
V =
V = 3.7 ft/sec

## Slide 99: Velocity vs Flow rates
Velocity = ft/sec
Flow = ft3/sec
Velocity: How fast water flows through a pipe in a given time; distance travelled per unit of time
- Feet per second (ft/s)
- Meters per sec (m/s)
Flow: Volume of water flowing through a pipe in a given time
- Gallons per minute (gpm)
- Cubic feet per second (ft3/sec)
- Million gallons per day (MGD)

## Slide 100: Flow
Your flow meter for your lift station pump is broken, but you want to figure out the pump's capacity. You open up the blow off and fill up 5-gallon buckets. You fill up 8 buckets in one minute. What is the capacity of your pump in GPM?
7
(A) 13 gal/min
(B) 40 gal/min
(C) 400 gal/min
(D) 130 gal/min
Flow = volume / time
Flow = 40 gal / minute
5 gallon

## Slide 101: Flow
What is the flow in gpm in an 18-inch diameter line when your rubber ducky is moving through it at a velocity of 2.5 ft/sec?
Flow = Velocity x Area
4.42 ft3
Flow = 2.5 ft/sec x 1.77 ft2
Conversion factors:
7.48 gallons = 1 ft3
60 secs = 1 min
Diameter = 18”
sec
60 sec
1 min
7.48 gals
1 ft3
=1984 gpm
V = 2.5 ft/sec
D= 18”
Flow = 4.42 ft3/sec
Diameter = 18”/12 = 1.5 ft
Area = 3.14 * r2
Area = 3.14 * (0.75 ft)2
Area = 3.14 * 0.56 ft2
Area = 1.77 ft2
Radius = 1.5 ft/2 = 0.75 ft

## Slide 102: Flow
What is the flow in gpm in a 12-inch diameter line when your rubber ducky is moving through it at a velocity of 1.1 ft/sec?
Flow = Velocity x Area
0.864 ft3
Flow = 1.1 ft/sec x 0.785 ft2
Conversion factors:
7.48 gallons = 1 ft3
60 secs = 1 min
Diameter = 12”
sec
60 sec
1 min
7.48 gals
1 ft3
= 388 gpm
V = 1.1 ft/sec
D= 12”
Flow = 0.864 ft3/sec
Diameter = 12”/12 = 1 ft
Area = 3.14 * r2
Area = 3.14 * (0.5 ft)2
Area = 3.14 * 0.25 ft2
Area = 0.785 ft2
Radius = 1 ft/2 = 0.5 ft
(A) 388 gal/min
(B) 9,293 gal/min
(C) 775 gal/min
(D) 1984 gal/min
8

## Slide 103: Detention Time

## Slide 104: Detention Time
The time water stays in a given reservoir or treatment process.

## Slide 105
4 Clarifiers = 40’ x 30’ x 21‘
Find the detention time in hours for the following WWTP: • 4 rectangular clarifiers each 40.0 ft long, 30.0 ft wide, and with an average water depth of 21.00 ft. • 1 oxidation ditch 295 ft long, 80.0 ft wide, and with a water depth of 11.0 ft. • Flow is 3.50 MGD

## Slide 106: Find the detention time in hours for the following WWTP: • 4 rectangular clarifiers each 40.0 ft long, 30.0 ft wide, and with an average water depth of 21.00 ft. • 1 oxidation ditch 295 ft long, 80.0 ft wide, and with a water depth of 11.0 ft. • Flow is 3.50 MGD
1 Oxidation Ditch = 295’ x 80’ x 11‘

## Slide 107
Vol of Oxidation Ditch = 1,942,000 gals
Vol of Clarifiers = 753,984 gals
Find the detention time in hours for the following WWTP: • 4 rectangular clarifiers each 40.0 ft long, 30.0 ft wide, and with an average water depth of 21.00 ft. • 1 oxidation ditch 295 ft long, 80.0 ft wide, and with a water depth of 11.0 ft. • Flow is 3.50 MGD

## Slide 108
Vol of WWTP = V = 2.7 MG
Flow = Q = 3.5 MGD
18.5 hours is the detention time for treatment in the WWTP.
Find the detention time in hours for the following WWTP: • 4 rectangular clarifiers each 40.0 ft long, 30.0 ft wide, and with an average water depth of 21.00 ft. • 1 oxidation ditch 295 ft long, 80.0 ft wide, and with a water depth of 11.0 ft. • Flow is 3.50 MGD

## Slide 109: Your secondary clarifier is 40 ft in diameter and 25 ft deep. Your max daily flow is 1.2 MGD. To determine if your clarifier meets the recommended detention time, you need to calculate the detention time of the clarifier in hours.
40ft
25ft
9
Diameter = 40 ft
Radius = 40 ft/2 = 20 ft
(A) 1 day
(B) 4.7 hours
(C) .20 days
(D) .20 hours
= 234,872 gal
Volume = π * r2 * Height
Volume = 3.14 * (20 ft)2 * 25 ft
Volume = 3.14 * 400 ft2 * 25 ft
Volume = 31,400 ft3
=4.7 hours
> 2-3 recommended design DT

## Slide 110: Detention Time Practice
A circular clarifier is being designed to accommodate an average flow of 76,250 gpd. To accommodate the space restrictions of the plant the diameter of the clarifier must not exceed 13 feet. What must the designed depth be to achieve a detention time of 2.5 hours?

## Slide 111: Practice: Combining all the concepts
Calculate the detention time of wastewater in hours as it flows through a rectangular aeration basin measuring 47 ft x 29 ft x 21 ft and 400 ft of pipe that is 18 inches in diameter. The wastewater velocity flowing through the pipe is 1.75 ft/second.
Tip: use the velocity to calculate flow rate, then use that to calculate detention time
V = 1.75 ft/sec
D= 18 in
400 ft
47 ft
21 ft
29 ft
*Not drawn to scale

## Slide 112: Practice: Combining all the concepts
Calculate the detention time of wastewater in hours as it flows through a rectangular aeration basin measuring 47 ft x 29 ft x 21 ft and 400 ft of pipe that is 18 inches in diameter. The wastewater velocity flowing through the pipe is 1.75 ft/second.
Tip: use the velocity to calculate flow rate, then use that to calculate detention time
V = 1.75 ft/sec
D= 18 in
400 ft
47 ft
21 ft
29 ft
*Not drawn to scale
Notes: Chanve V to 28,623

## Slide 113: Practice: Combining all the concepts
Calculate the detention time of wastewater in hours as it flows through a rectangular aeration basin measuring 47 ft x 29 ft x 21 ft and 400 ft of pipe that is 18 inches in diameter. The wastewater velocity flowing through the pipe is 1.75 ft/second.
Tip: use the velocity to calculate flow rate, then use that to calculate detention time
V = 1.75 ft/sec
D= 18 in
400 ft
47 ft
21 ft
29 ft
*Not drawn to scale
DT
Notes: Chanve V to 28,623

## Slide 114: Weir Loading Rate
Measures the amount of water leaving a settling tank per linear unit of length of weir per day
Used to ensure weirs are not hydraulically overloaded, efficient sedimentation is occurring and solids do not infiltrate clarifier effluent
Recommended 10,000-20,000 gpd/ft (124,100-248,200 Lpd/m)
Typically correlates with a correct detention time
**Use “weir” as indicator that weir length is involved**

## Slide 115: Weir Loading Rate Example
The flow for a circular clarifier is 1.2 MGD with a 26-foot diameter. What is the weir overflow rate in gallons per foot of weir length per day?

## Slide 116: Weir Loading Rate Practice 1
A rectangular sedimentation tank with a length of 12 ft, a width of 18 ft, and a depth of 11 ft has a flow of 190,000 gpd. What is the weir overflow rate of this this sedimentation tank if influent enters on one wide side of the tank and effluent exits on the other?
18 ft
12 ft

## Slide 117: Weir Loading Rate Practice 2
A circular clarifier that treats an average of 4,000 per day of wastewater has a diameter of 11-meters and a depth of 4-meters. What is the weir overflow rate of the clarifier in Lpd/m?

## Slide 118: Surface Loading Rate
Measures the amount of water passing over a unit of surface area per day
Another parameter that indicates clarifiers are not hydraulically overloaded and has a direct relationship to the settleable solids removal efficiency of sedimentation tanks
Recommended 300-1,200 gpd/ (12,160-48,645 Lpd/)
**Use “surface” as indicator that surface area is involved**

## Slide 119: Surface Loading Rate Example
What is the surface loading rate of a circular clarifier with a depth of 8.0 ft, a diameter of 9.0 ft and an effluent flow of 42,000 gpd?

## Slide 120: Surface Loading Rate Practice 1
What is the surface loading rate of a rectangular clarifier in Lpd/ with a length of 26 m, a width of 9.0 m, and a depth of 14 m. The clarifier treats on average, 10,500 cubic meters of influent per day.
Notes: 234

## Slide 121: Surface Loading Rate Practice 2
A known design parameters for a rectangular clarifier are listed below. What is the surface loading rate in gal/ft2*day? What is the depth required to maintain a maximum detention time of 3.0 hours?
Knowns:
Q= 2.2 MGD
L= 72 ft
W= 28 ft

## Slide 122: Biological Treatment Calculations
Notes: 60 Min-
Likely 60 Min- 9 Questions
BOD COD TSS RBC Trickling Filters

## Slide 123: Percent Removal
%

## Slide 124: Percent Removal
The amount of a contaminant removed in percent form.
Helps determine if effluent meets NPDES limits
Helps inform if WWTP is doing its job.
Allows comparison of actual conditions with design specifications.

## Slide 125: The iron content of a wastewater is 1.81mg/L. What is the percent removal if the effluent wastewater contains 0.11 mg/L iron?
Raw water iron (In) = 1.81 mg/L
Finished water iron = 0.11 mg/L (Out)
94% is the percent removal of iron in the finished water.

## Slide 126: You operate a surface water treatment plant and one of the SDWA requirements as part of the DBPR is to remove a certain percentage of Total Organic Carbon. If your raw water TOC is 3.2 mg/L and your finished water TOC is 0.9 mg/L, calculate the percent removal for TOC.
Raw water TOC (In) = 3.2 mg/L
Finished water TOC = 0.9 mg/L (Out)
72% is the percent removal of TOC in the finished water.

## Slide 127: BOD Equations

## Slide 128: BOD Problem Example
The dissolved oxygen of a sample from a WWTP’s treated effluent was measured shortly after collection and after being incubated at 20°C for 5 days and the following data was produced. Calculate the BOD5.
Sample | Blank | Effluent
Sample Volume | N/A | 50 mL
Seed Volume | N/A | N/A
Initial DO | 9.1 mg/L | 9.1 mg/L
DO after 5 days | 8.9 mg/L | 5.5 mg/L
Blank 5-day change should be <0.2 mg/L

## Slide 129: BOD Problem Example 2
BOD tests were performed on a sample of WWTP influent and control laboratory control bottles. Calculate the of the plant influent based on the following data:
Sample | Blank | Influent | Seed Blank
Sample Volume | N/A | 5 mL | 0 mL
Seed Volume | N/A | 1 mL | 3 mL
Initial DO | 8.0 mg/L | 8.0 mg/L | 8.0 mg/L
DO after 5 days | 7.9 mg/L | 3.6 mg/L | 6.8 mg/L

## Slide 130: BOD Practice Problem 1
The dissolved oxygen of a primary effluent sample was measured shortly after collection and after being incubated at 20°C for 5 days and the following data was produced. Calculated the BOD5.
Sample | Effluent
Sample Volume | 10 mL
Seed Volume | N/A
Initial DO | 8.0 mg/L
DO after 5 days | 3.7 mg/L

## Slide 131: BOD Practice Problem 2
BOD tests were performed on a sample of WWTP effluent and control laboratory control bottles. Calculate the of the plant influent based on the following data:
Sample | Blank | Influent | Seed Blank
Sample Volume | N/A | 150 mL | 0 mL
Seed Volume | N/A | 1 mL | 3 mL
Initial DO | 7.9 mg/L | 7.9 mg/L | 7.9 mg/L
DO after 5 days | 7.9 mg/L | 2.1 mg/L | 5.5 mg/L
= 0.8 mg/L

## Slide 132: Organic Loading Rate Example
An RBC has an influent flow of 150,000 gal/day with a BOD concentration of 180 mg/L. The total media surface area is 60,000ft2. Calculate the organic load in lbs/day/1000 ft2 of media surface.
The information needed isn’t provided, so we have to find it with what we know. First calculate the organic load in lb/day:
BOD (lb/day) = (BOD concentration (mg/L) * Flow (MGD) * 8.34 lb/gal)
BOD (lb/day) = (180 mg/L) * Flow (MGD) * 8.34 lb/gal)
BOD (lb/day) = (180 mg/L * 0.15 MGD * 8.34 lb/gal)
BOD (lb/day) = 225.18 lb/day
=0.15 MGD

## Slide 133: Organic Loading Rate Example Cont.
Rotating Biological Contactor (RBC)
An RBC has an influent flow of 150,000 gal/day with a BOD concentration of 180 mg/L. The total media surface area is 60,000ft2. Calculate the organic load in lbs/day/1000 ft2 of media surface.
The information needed isn’t provided, so we have to find it with what we know.
Calculate the surface area in :
Unit Conversion
Now you can fill in the equation for Organic Loading Rate:
Organic Loading Rate = 3.75 lb/day/1,000ft2
Typical organic loading of an RBC is 2.5 to 4 lbs BOD/day/1000 ft2.

## Slide 134: Organic Loading Rate Example 2
A flow of 1.5 MGD is applied to a trickling filter with a diameter of 48 ft and a depth of 5 ft. The incoming BOD concentration is 130 mg/L. Calculate the organic loading on the filter in lb/day/1000 ft3 of media.
We are not provided the organic load or the media volume. How do we get those?

## Slide 135: Organic Loading Rate Example 2 Cont.
A flow of 1.5 MGD is applied to a trickling filter with a diameter of 48 ft and a depth of 5 ft. The incoming BOD concentration is 130 mg/L. Calculate the organic loading on the filter in lb/day/1000 ft3 of media.
9,043.2 ft3
Organic Loading Rate = 180 lb/day/1,000

## Slide 136: Organic Loading Rate Practice Problem
An RBC receives a flow of 385,000 gpd with a BOD of 185 mg/L. What is the organic loading rate for the RBC if the surface area of the media is 225,000?

## Slide 137: Organic Loading Rate Equations Cont’d
Lagoon Ponds

## Slide 138: Organic Loading Rate Example 3
A flow of 500,000 gpd enters a wastewater pond with an average length of 600 ft and an average width of 400 ft. The incoming BOD concentration is 150 mg/L. Calculate the organic loading in the pond in lb/day/acre.
We are not provided the organic load or pond’s surface area. How do we get those?

## Slide 139: Organic Loading Rate Example 3 Cont.
A flow of 500,000 gpd enters a wastewater pond with an average length of 600 ft and an average width of 400 ft. The incoming BOD concentration is 150 mg/L. Calculate the organic loading in the pond in lb/day/acre.
625.5
Organic Loading Rate = 114 lb/day/ac
/ 43,560 /acre = 5.5 ac

## Slide 140: Hydraulic Loading Rate
Measures the amount of wastewater applied to a treatment system per unit of area per day
Used as a design parameter to ensure processes can handle the expected flow and will not be overloaded
Performance monitoring indicator
Applies to: Trickling Filter
RBCs
Lagoons
Constructed Wetlands
Expressed in gpd/ and /day/

## Slide 141: Hydraulic Loading Rate Equations

## Slide 142: Hydraulic Loading Rate Example
A flow of 0.5 MGD is applied to a trickling filter with a diameter of 20 ft and a depth of 5 ft. The incoming BOD concentration is 130 mg/L. Calculate the hydraulic loading on the filter in gpd/ft2.
Given:
Flow MGD
Diameter
Depth
Concentration
Need:
Flow gpd
Area
Need:
Flow: conversion from MGD to gpd
Area: formula to calculate it

## Slide 143: Hydraulic Loading Rate Example Cont.
A flow of 0.5 MGD is applied to a trickling filter with a diameter of 20 ft and a depth of 5 ft. The incoming BOD concentration is 130 mg/L. Calculate the hydraulic loading on the filter in gpd/ft2.
Convert Flow, gal/day = = 500,000gpd
1,592
314

## Slide 144: Hydraulic Loading Rate Practice Problem
Calculate the hydraulic loading rate on a trickling filter with an influent flow rate of 200,000 gpd and a recirculation rate of 400,000 gpd. The media surface area is 1,445 ft2.
gpd/ft2

## Slide 145: Multi-Question Pond Problem
Pulling it all together

## Slide 146: For a wastewater pond:
Calculate
  Time to fill the pond
  Population Loading
  Organic Loading
  Hydraulic Loading
Think through
  What units will you need?
  Time to fill the pond = detention time (volume and flow rate)
  Loadings require areas
Knowns
  Average Depth = 4 ft
  Average Width = 420 ft
  Average Length = 580 ft
  Flow = 400,000 gpd
  BOD = 150 mg/L
  Population = 4,000 persons

## Slide 147: Initial Calculations to Perform
Area
Volume
Loading Rate
Length x Width
580 ft x 420 ft
243,600 ft2
4 ft
May need to convert to acres: 5.6 acres
May need to convert to gallons: 7,288,512 gal

## Slide 148: Solutions
Time to fill the pond
Population Loading
= 4,000 people / 5.6 acres = 714 people/ac
Organic Loading
Hydraulic Loading
= 500.4lb/day / 5.6ac = 89.4 lb/day/ac

## Slide 149: Dosing Rate (Spülkraft Rate)
Used to control the film thickness in trickling filters
Incorporates hydraulic loading rate and rotating distributor speed
Increasing trickling filter dosage rates provides hydraulic sheer that removes the outer biofilm layer
Expressed as in/pass and mm/pass
Notes: Biofilms that are too thick are not treating wastewater at the base, so increasing the dosing rate helps removal unnecessary biofilm. Oxygen and organic matter do not penetrate more than ~1mm into the biofilm.
You can directly manipulate the dosing rate by adjusting the HLR, which can be adjusted by increasing circulation and the dosing rate is indirectly manipulated by increasing the number of distribution arms (through design or refurbishment) or increasing the rotational speed of the distribution arm

## Slide 150: Dosing Rate Example
Determine the dosing rate in inches per pass of a trickling filter with 4 arms operated at a hydraulic loading rate of 550 gallons per square foot of media per day. The rotational speed of the arms is 1 revolution per minute.
15

## Slide 151: Dosing Rate Practice Problem
Determine the dosing rate in inches per pass of a trickling filter with 2 arms operated at a hydraulic loading rate of 300 gallons per square foot of media per day. The rotational speed of the arms is 1.2 revolutions per minute.
14

## Slide 152: Recirculation Ratio
Process of recycling effluent back through the tricking filter
Recirculation is considered the most important parameter for trickling filter operation
Increased to dilute wastewater, increase sloughing, prevent pests, etc.
Decreased to prevent icing, etc.
Recirculation assessed by comparing rate of recirculated flow compared to influent flow

## Slide 153: Recirculation Ratio Example
A trickling filter receives a flow of 192,000 gpd. If the trickling filter effluent is recirculated at the rate of 225,000 gpd, what is the recirculation ratio?

## Slide 154: Recirculation Ratio Practice Problem
A trickling filter receives a flow of 238,000 gpd. If the trickling filter effluent is recirculated at the rate of 0.28 MGD, what is the recirculation ratio?
The units don’t match!
Convert 238,000 gpd to MGD by dividing by 1,000,000

## Slide 155: Hydraulic Retention Time
Measures the amount of time it takes a given amount of wastewater to pass through a treatment tank at a given flow rate
Equivalent to detention time
Expressed in hours
Operation parameter for: RBCs
Activated Sludge

## Slide 156: Hydraulic Retention Time Example
A wastewater treatment tank has a volume of 200,000 gallons and a flow rate of 100gpm. What is the HRT?

## Slide 157: Hydraulic Retention Time Practice
A wastewater treatment tank is 20 feet in diameter and 5 feet deep and has a flow rate of 10gpm. What is the HRT?
We have to calculate the volume
And convert to gallons
1,570.2 ft3

## Slide 158: Other Examples
Media substrate removal flux
Tank substrate removal flux
Etc
Maybe just use one of these equations to practice identifying equation, what we’re looking for and variables

## Slide 159: Chemical Dosing
Notes: 30 Min
5 Questions

## Slide 160: Chlorine Disinfection
Disinfection is used to remove all disease causing pathogens from effluent before it is discharged to receiving waters
Disinfection is accomplished with liquid (sodium hypochlorite), solid (calcium hypochlorite), and gas chlorine
Typical Chlorine Disinfection Calculation Variables:
Chlorine Dosage
Chlorine Demand
Chlorine Residual
All Concentrations
Notes: Chlorine Dosage- Amount of Chlorine added to water. Calculated by dividing the chlorine feed by the flow or volume
Chlorine Demand- Amount of Chlorine required to act with all reactive substances in the flow
Chlorine residual- Remaining Chlorine in the water after demand has been satisfied

## Slide 161: Chlorine Solution Strength
Liquid Bleach = 3-12% available chlorine
HTH = 65-70% available Chlorine

## Slide 162: Solution Strength Practice Problem
Your wastewater treatment plant uses a 4% solution to disinfect treated wastewater. What is the strength of the solution expressed as a decimal?

## Slide 163: Chlorine Residual
1) Chlorine Dosage = Chlorine Demand + Chlorine Residual
2) Residual = Dosage – Demand
3) Demand = Dosage - Residual
Residual composed of free Chlorine and combined Chlorine
  Free Chlorine- unreacted Chlorine reacts with H2O to form hypochlorous and hydrochloric acid
  Combined Chlorine- In the presence of ammonia, hypochlorous acid forms chloramines
  Measurement of remaining chlorine after it is utilized for disinfection
Notes: The one you would actually most likely use to calculate in the field is your chlorine demand, because the other two are measured.
The feed rate can be used to calculate dosage or if it’s in the form of a liquid the solution can be measured with a meter.
Chlorine residual is measured with a field concentration test or in a lab.

## Slide 164: Chlorine Dosage Practice
Determine the chlorine demand of a treated wastewater effluent if the chlorine dosage used for disinfection is 8 mg/L and the measured chlorine residual is 1.3 mg/L.

## Slide 165: Chlorine Dosage from Feed Rate

## Slide 166: Chlorine Feed Example 1
A chlorinator is set to feed 417 lbs/day of 12% chlorine bleach to treat a flow of 2 MGD. What will be the resulting chlorine dosage in mg/L?
0.12

## Slide 167: Chlorine Fee Practice Problem
A wastewater treatment plant with a flow of 15 MGD has determined that their disinfection process has a chlorine demand of 4.3 mg/L. Their NPDES permit requires that they maintain a chlorine residual of 1.5 mg/L. What must the minimum solution strength of their chlorine solution (as a percentage) be if the maximum feed rate of their equipment is 475 lbs/day?

## Slide 168: Chemical Feed

## Slide 169: Dechlorination
Sulfur dioxide () is used to dechlorinate treated wastewater
Molecular weight of ≈
Can be used at a 1 to 1 ratio
A safety factor of 3 mg/L is typically applied to sulfur feed calculations

## Slide 170: Sulfur Feed Rate Example
A wastewater treatment plant with a 2.0 MGD flow has an average chlorine residual of 4.5 mg/L after disinfection treatment. What is the sulfur feed rate required to properly dechlorinate the wastewater, if a safety factor of 3 mg/L is desired?

## Slide 171: Ozone () Disinfection
Ozone is a powerful oxidizing agent and destroys virus more effectively than chlorine.
Typical ozone math examples:
Calculating the ozone demand
Dosage
Notes: Ozone demand is done in the same way as chlorine demand. The residual is subtracted form the dosage.
Dosage is

## Slide 172: Ultraviolet (UV) Disinfection
UV lamps produce UV radiation with a wavelength = 254 nm
Notes: Important figures and formulas to remember for UV disinfection
This wavelength penetrates microorganisms and alters their DNA so they can no longer reproduce
Lamp Arc Length is not necessarily the length of the lamps themselves and instead depend on different optical factors and would most likely be given.

## Slide 173: Bacterial Density

## Slide 174: Motor and Electrical Calculations
Notes: 60 Min
Likely 45 Minutes
SVI, F:M, MCRT/SRT, Return Sludge Rate
Optional Recirc Rates etc.

## Slide 175: Work and Power
Work- The Exertion of force over a specific distance
Lifting a 1-lb object one foot (1 foot-lb)
Power- The measure of how much work is done over a give amount of time
Lifting that object over a 1-minute time span
Watts, HP, etc.
1 HP = 746 Watts = 33,000

## Slide 176: Work and Power
Watts is the unit of power for electrical applications
, useful for electricity costs

## Slide 177: Power Example
A 220-volt motor pulls 84 amps during operation. What is the power requirement for this motor in watts? In horsepower?

## Slide 178: Activated Sludge Analysis Scenario
An operator at a wastewater treatment plant observes a couple of concerning characteristics at the activated sludge plant. The BOD and TSS concentrations in the plants effluent are approaching the plants NPDES permit limits and the operator also observes increased thick foaming at the surface of the aeration tank instead of the crisp white foam usually produced by the dissolved oxygen. The operator decides to collect some operational data and perform an SVI analysis to identify the issue. After 30 minutes the sludge volume of a 1 L sample was measured at 700 mL. Use the collected data to calculate the F:M ratio, SVI, and SRT for this system. Based on this information, what may be causing these issues at the plant and what adjustments can the operator make to address them?
Aeration Basin Volume | Vab | 100,000 gal
Secondary Clarifier Volume | Vsc | 44,000 gal
Influent Flow | Q | 265,000 gpd
Waste Sludge Flow | QWAS | 8,000 gpd
Mixed Liquor Suspended Solids | MLSS | 2400 mg/L
Waste Sludge Suspended Solids | TSSWAS | 8100 mg/L
Final Effluent Suspended Solids | TSSeff | 6 mg/L
Secondary Clarifier Suspended Solids | TSSsc | 500 mg/L
Influent BOD | BOD | 340 mg/L
Biomass percentage of mixed liquor |  | 85%

## Slide 179: Activated Sludge Analysis Scenario
Settled Sludge Volume = 700 mL
Aeration Basin Volume | Vab | 100,000 gal
Secondary Clarifier Volume | Vsc | 44,000 gal
Influent Flow | Q | 265,000 gpd
Waste Sludge Flow | QWAS | 8,000 gpd
Mixed Liquor Suspended Solids | MLSS | 2400 mg/L
Waste Sludge Suspended Solids | TSSWAS | 8100 mg/L
Final Effluent Suspended Solids | TSSeff | 6 mg/L
Secondary Clarifier Suspended Solids | TSSsc | 500 mg/L
Influent BOD | BOD | 340 mg/L
Biomass percentage of mixed liquor |  | 85%
Notes: F:M = 0.44, SVI = 292, SRT = 3.95 days